## Cover
BILL OF QUANTITIES
ELECTRICAL POWER DISTRIBUTION WORKS — DEWA AUTHORITY
Project | Proposed B+G+8+R Commercial & Residential Building
Owner / Client | Qutaiba Ameen Abdal Kija
Plot No. | 6731315 — Al Barsha South Third, Dubai, UAE
MEP Consultant | Future Art Engineering Consultancy
Authority | DEWA (Dubai Electricity & Water Authority)
TENDER DETAILS
Job No. | FA_P379 / CRs B/010/25
Drawing Ref | P-001 … P-300 (14 sheets, Power)
Drawing Date | 19/06/2026
BOQ Date | 19/06/2026
Addendum No. | 0
BOQ Status | PRICED (INDICATIVE) — Dubai 2026 rates · POWER scope · review before submission
Currency | AED (UAE Dirham)
VAT Rate | 5% (UAE Federal)
CONTRACTOR DETAILS
Contractor | SABI Engineering & Contracting LLC
Address | Dubai, United Arab Emirates
Phone | +971 4 XXX XXXX
Email | estimation@sabi.ae
TRN | 100XXXXXXXXXXXXX
LIST OF BILLS
Bill | Description |  |  | Sheet
1 | General Items / Preliminaries |  |  | Bill 1
2 | HV / LV Main Distribution (Transformer, MDB, Generator, ATS, Capacitors) |  |  | Bill 2
3 | Sub-Main Distribution Boards (SMDBs) |  |  | Bill 3
4 | Distribution Boards (DBs) & Consumer Units |  |  | Bill 4
5 | LV Power Cables (Main + Distribution + Final Circuits) |  |  | Bill 5
6 | Cable Containment (Tray, Ladder, Trunking, Conduit) |  |  | Bill 6
7 | Wiring Devices & Accessories |  |  | Bill 7
8 | Lighting Fixtures (Internal + External) |  |  | Bill 8
9 | Earthing & Lightning Protection |  |  | Bill 9
10 | Emergency Lighting & Life Safety |  |  | Bill 10
11 | ELV Containment (Telephone, Data, CCTV, ACS, MATV, FA) |  |  | Bill 11
12 | Metering & Monitoring |  |  | Bill 12
13 | Testing, Commissioning & DEWA Approval |  |  | Bill 13
COMPLIANCE SUMMARY — what this BOQ already covers
✓ DEWA Distribution Standards · Dubai Municipality (DM) · Dubai Civil Defence (DCD) — see Preamble Sheet § 0 Statutory Compliance
✓ DEWA Smart Metering programme — Bill 12 (smart kWh meters single + three-phase, AMI-ready, MDM integration, Shams Dubai bi-directional, IEC 62052/62053)
✓ UAE Federal VAT (5 %) — line on Summary of Bills sheet, computed via Excel formula on the pre-VAT total
✓ Authority Fees & NOCs — Bill 1.5 (DEWA connection / load-letter / energising · RTA road permit · DM completion fee · DCD NOC fee)
✓ Central Battery System (CBS) — Bill 10.3 as alternative to self-contained luminaires; Fire Alarm / MEP integration — Bill 10.4 (shunt-trips, lift recall, dampers, mag-locks)
✓ All ~280 priceable line items pre-priced with INDICATIVE Dubai 2026 rates — review each line against actual supplier quotation before submission
✓ Origin / Brand column (H) pre-populated with Dubai AVL bands (Schneider/ABB/Siemens, Ducab/NCC, Itron/L+G, etc.) — overwrite with selected make at tender time
✓ Drawing references (column C) mapped to specific P-001 … P-300 sheet numbers per item type (SLD / floor plan / LV-room / cable-tray detail)
✓ Engineering corrections from PDF_vs_XLSX_Comparison.pdf applied: LVP-01 risers 150mm² · fire pump 185mm² FR · ESMDB-G 300mm² FR · building totals on Cover
DATA PROVENANCE — measured from project drawings vs industry allowance
📐 MEASURED | derived from project drawings (P-001 … P-300) via the AI extraction — quantities and counts are project-specific
📋 ALLOWANCE | industry-standard template / fixture default — quantities are allowances based on building size, NOT counted from drawings — review before submission
Bill | Description | Source | Notes
Bill 1 | Preliminaries + Authority Fees | 📋 ALLOWANCE | Industry allowance (mob, insurance, submittals, DEWA/RTA/DM/DCD fees)
Bill 2.1 | HV side (transformer / RMU / room civil) | 📋 ALLOWANCE | Industry template — transformer kVA sized from MD only
Bill 2.2 | LV panels (LVP-01, LVP-02) | 📐 MEASURED | From P-200 SLD — ACB ratings, MCCB schedules, capacitor banks
Bill 2.3 | Generator + ATS | 📐 MEASURED | From P-200 SLD — kVA + ATS rating
Bill 3 | Sub-Main Distribution Boards (26) | 📐 MEASURED | From P-201 SLD — every SMDB tag, rating, floor, connected load
Bill 4 | Distribution Boards (107) | 📐 MEASURED | From P-103…P-108 floor plans + P-201 SLD — DB groups, counts
Bill 5.1 | XLPE LV→SMDB risers | 📐 MEASURED | From cable_schedule — every run, size, length per AI extraction
Bill 5.2 | Fire-Rated LV→SMDB | 📐 MEASURED | From cable_schedule — with engineering corrections applied
Bill 5.3 | XLPE SMDB→DB distribution | 📐 MEASURED | From smdb_to_db_cables / cable_schedule (non-LV-source filter)
Bill 5.4 | FR SMDB→DB distribution | 📐 MEASURED | From smdb_to_db_cables / cable_schedule
Bill 5.5 | LSZH escape-route final circuits | 📋 ALLOWANCE | Industry allowance — quantities by floor count × typical loop
Bill 5.6 | Final-circuit bulk wiring | 📋 ALLOWANCE | Industry allowance — by sqft / DB count
Bill 5.7 | ECC alongside risers | 📋 ALLOWANCE | Allowance — derived as % of main-cable total length
Bill 6 | Cable containment | 📋 ALLOWANCE | Industry allowance — tray / ladder / conduit lengths by sqft
Bill 7 | Wiring devices & accessories | 📋 ALLOWANCE | Industry template — sockets / switches / outlets per typical floor count
Bill 8 | Lighting fixtures | 📋 ALLOWANCE | Industry template — no fixture legend read from drawings
Bill 9 | Earthing & Lightning Protection | 📋 ALLOWANCE | Industry allowance — TN-S system + LP per IEC 62305
Bill 10.1 | Self-contained emergency luminaires | 📋 ALLOWANCE | Industry allowance — by floor count + escape route length
Bill 10.2 | Life-safety power feeders | 📋 ALLOWANCE | Industry allowance — fire pump / smoke / pressurisation
Bill 10.3 | Central Battery System (CBS) | 📋 ALLOWANCE | Industry option — provisional sum, sized to total emergency luminaire load
Bill 10.4 | Fire Alarm / MEP integration | 📋 ALLOWANCE | DCD requirement — shunt-trips, lift recall, dampers (specialist coord)
Bill 11 | ELV containment | 📋 ALLOWANCE | Industry allowance — specialist trades (FA / BMS / CCTV / ACS / MATV)
Bill 12 | Smart metering | 📋 ALLOWANCE | DEWA Smart Grid programme — meter counts per tenant + landlord schedule
Bill 13 | Testing, Commissioning & Authority | 📋 ALLOWANCE | Industry allowance — IR / continuity / ELI / RCD + DEWA + DM + DCD
STATUS: PRICED (INDICATIVE) — Dubai 2026 rates · POWER scope · review before submission

## Preamble & Standards
PREAMBLE & APPLICABLE STANDARDS
0. STATUTORY COMPLIANCE — UAE / DUBAI AUTHORITIES
The works under this BOQ shall fully comply with the requirements of the following Dubai and UAE authorities. The contractor shall obtain all approvals, attend witnessed inspections, and submit all documentation required by each authority as part of the contract.
Authority | Scope of compliance
DEWA | Dubai Electricity & Water Authority — Distribution Standards, Service Connection Specifications, Smart Grid / Smart Metering programme, witnessed inspections, energising, meter sealing, As-Built filing.
Dubai Municipality | Building Code, Local Order 89/1994 (Building Regulations) and amendments, electrical safety inspections, occupancy / completion certificate clearance.
DCD | Dubai Civil Defence — UAE Fire & Life Safety Code of Practice (latest edition); fire-rated containment, FR/LSZH cable selection, emergency lighting, fire-fighter's lift, smoke-control fan power supplies.
UAE Federal | Federal Tax Authority — VAT (5%) per UAE VAT Law (Federal Decree-Law No. 8 of 2017); MoCCAE / ESMA conformity certificates for electrical equipment placed on UAE market.
1. SCOPE OF WORKS
Supply, installation, testing and commissioning of the complete LV electrical distribution system, lighting, small power, earthing & lightning protection, metering and life-safety related electrical installations for the project, in accordance with the tender drawings, specifications, applicable standards, and authority requirements (DEWA, Dubai Municipality, Dubai Civil Defence). The scope shall include all materials, labour, plant, supervision, transport, scaffolding, builder's work in connection, testing instruments, commissioning, As-Built drawings and O&M manuals.
2. APPLICABLE STANDARDS
Standard | Description
DEWA | Distribution Standards & Authority Regulations (latest edition)
DEWA Smart Grid | Smart Metering Programme / AMI Specifications / Shams Dubai
DM | Dubai Municipality Building Code & Electrical Inspection Standards
DM Local Order | Local Order 89/1994 — Building Regulations and amendments
DCD | Dubai Civil Defence — UAE Fire & Life Safety Code of Practice (latest)
BS 7671 | IEE Wiring Regulations (18th Edition / latest)
IEC 60364 | Low-voltage electrical installations
IEC 60439 | LV switchgear and controlgear assemblies (Form separation)
IEC 60947 | LV switchgear (ACBs, MCCBs, contactors)
IEC 60331 | Fire-resisting characteristics of electric cables
BS 6387 CWZ | Performance requirements for fire-rated cables
BS 7211 | LSZH (Low Smoke Zero Halogen) cable performance
IEC 60332-3 | Cable flame-propagation test (Cat A/B/C)
IEC 61034 / 60754 | Smoke density / halogen-acid gas emission tests for LSZH cables
BS 4444 | Earth electrode resistance test method
IEC 62305 | Lightning protection systems
IEC 62052/62053 | Electricity metering equipment — general requirements
Dubai GBR | Dubai Green Building Regulations & Specifications
UAE FTA | Federal Tax Authority — VAT (5%) on tender total per Federal Decree-Law 8/2017
3. ABBREVIATIONS
Abbr. | Meaning
ACB | Air Circuit Breaker
MCCB | Moulded Case Circuit Breaker
MCB | Miniature Circuit Breaker
RCD | Residual Current Device
LVP | LV Panel (Main)
SMDB | Sub-Main Distribution Board
ESMDB | Emergency SMDB
DB | Distribution Board
EDB | Emergency DB
ATS | Automatic Transfer Switch
XLPE | Cross-Linked Polyethylene
SWA | Steel Wire Armoured
FR | Fire Rated (BS6387 CWZ)
ECC | Earth Continuity Conductor
MEB | Main Earth Bar
LP | Lightning Protection
T&C | Testing & Commissioning
SLD | Single Line Diagram
TCL | Total Connected Load
MD | Maximum Demand
DF | Demand Factor
PF | Power Factor
kVA | Kilo-Volt-Ampere
kW | Kilo-Watt
kVAR | Kilo-Volt-Ampere Reactive
IP55/IP65 | Ingress Protection ratings
4. PRICING NOTES
(1) | All rates shall include supply, delivery, off-loading, storage, installation, fixings, support steelwork, painting, identification labelling, testing, commissioning, and handover.
(2) | All quantities are estimated from tender drawings; the contractor shall verify on site before procurement. No claim for variation will be entertained for take-off discrepancies within ±5% of the BOQ quantity.
(3) | Cable lengths include +10% installation allowance (vertical rise + horizontal route + termination + slack).
(4) | Where a "lot" or "item" unit is used, the rate shall cover the complete scope described in that item including all incidentals.
(5) | Provisional sums (PS) are net rates; the contractor shall add a percentage for overheads, profit, and attendance separately at the foot of each Bill where applicable.
(6) | All prices shall be in UAE Dirhams (AED), exclusive of VAT. VAT at 5% will be added at the foot of the Summary in accordance with UAE Federal Tax Authority requirements.
(7) | Rates shall remain firm and fixed for the duration of the contract including the Defects Liability Period unless otherwise agreed in writing.

## Bill 1 - Preliminaries
BILL No. 1 — GENERAL ITEMS / PRELIMINARIES
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
1.1 — PROJECT MOBILISATION & SITE ESTABLISHMENT
1.1.1 | Mobilisation to site, including transport of plant, tools, materials and personnel. | — | Sum | 1 | 125000 |  | 📋 — (contractor selection)
1.1.2 | Site offices, storage compounds, sanitary and welfare facilities for the duration of the works. | — | Sum | 1 | 85000 |  | 📋 — (contractor selection)
1.1.3 | Site hoarding, fencing and security as per main contractor / consultant requirements. | — | Sum | 1 | 35000 |  | 📋 — (contractor selection)
1.1.4 | Health & Safety plan, PPE, fall-arrest and electrical safety (LOTO) provisions for the duration. | — | Sum | 1 | 18000 |  | 📋 — (contractor selection)
1.1.5 | Coordination with main contractor and other MEP trades — shop-drawing review meetings, BIM coordination as required. | — | Sum | 1 | 25000 |  | 📋 — (contractor selection)
Sub-Total 1.1
1.2 — INSURANCE & BONDS
1.2.1 | Contractor's All Risks (CAR) insurance for the contract value, full duration plus DLP. | — | Sum | 1 | 85000 |  | 📋 — (contractor selection)
1.2.2 | Workmen's Compensation and Public Liability insurance. | — | Sum | 1 | 45000 |  | 📋 — (contractor selection)
1.2.3 | Performance bond (10% of contract value) — bank guarantee in favour of the employer. | — | Sum | 1 | 18000 |  | 📋 — (contractor selection)
1.2.4 | Advance payment guarantee — bank guarantee against advance. | — | Sum | 1 | 12000 |  | 📋 — (contractor selection)
Sub-Total 1.2
1.3 — TEMPORARY UTILITIES & TESTING INSTRUMENTS
1.3.1 | Temporary power supply during construction — generator, distribution, metering, fuel. | — | Sum | 1 | 85000 |  | 📋 — (contractor selection)
1.3.2 | Temporary lighting in areas of work as required for safe execution. | — | Sum | 1 | 25000 |  | 📋 — (contractor selection)
1.3.3 | Provision of all testing instruments — Megger 500V/1000V, earth tester, multimeter, RCD tester, loop tester, calibration certificates current. | — | Sum | 1 | 5500 |  | 📋 — (contractor selection)
Sub-Total 1.3
1.4 — SUBMITTALS, AS-BUILTS, O&M MANUALS
1.4.1 | Shop drawings (AutoCAD) — full set, multiple revisions until approved. | — | Sum | 1 | 85000 |  | 📋 — (contractor selection)
1.4.2 | Material approval submittals — datasheets, samples, manufacturer's certificates, country-of-origin declarations. | — | Sum | 1 | 35000 |  | 📋 — (contractor selection)
1.4.3 | As-Built drawings (AutoCAD + PDF, 4 hard copies) at handover. | — | Sum | 1 | 45000 |  | 📋 — (contractor selection)
1.4.4 | Operation & Maintenance manuals (4 hard copies + PDF) at handover, including spare-parts list. | — | Sum | 1 | 38000 |  | 📋 — (contractor selection)
1.4.5 | Defects Liability Period support (12 months from handover) — site attendance, replacement of defective materials, retesting. | — | Sum | 1 | 12000 |  | 📋 — (contractor selection)
Sub-Total 1.4
1.5 — AUTHORITY FEES, NOCs & PERMITS
1.5.1 | DEWA HV/LV connection capacity charges (per kVA, DEWA tariff). Provisional sum — final amount per DEWA load-letter response. | DEWA / DM / DCD / RTA tariff | Sum | 1 | 350000 |  | 📋 DEWA / DM / DCD / RTA
1.5.2 | DEWA load-letter application & approval fees (capacity allocation, RMU/substation siting, voltage level confirmation). | DEWA / DM / DCD / RTA tariff | Sum | 1 | 8000 |  | 📋 DEWA / DM / DCD / RTA
1.5.3 | DEWA energising application fee — submission, processing, witness arrangement, meter sealing. | DEWA / DM / DCD / RTA tariff | Sum | 1 | 12000 |  | 📋 DEWA / DM / DCD / RTA
1.5.4 | RTA road-cutting permit + reinstatement (where HV/LV cabling crosses public road or pavement). Provisional sum. | DEWA / DM / DCD / RTA tariff | Sum | 1 | 45000 |  | 📋 DEWA / DM / DCD / RTA
1.5.5 | Dubai Municipality (DM) electrical inspection & completion-certificate fee — for occupancy / completion sign-off. | DEWA / DM / DCD / RTA tariff | Sum | 1 | 18000 |  | 📋 DEWA / DM / DCD / RTA
1.5.6 | Dubai Civil Defence (DCD) electrical clearance NOC fee — life-safety clearance for fire pump, smoke control, emergency lighting. | DEWA / DM / DCD / RTA tariff | Sum | 1 | 12000 |  | 📋 DEWA / DM / DCD / RTA
Sub-Total 1.5
BILL 1 — TOTAL CARRIED TO SUMMARY

## Bill 2 - HV-LV Main
BILL No. 2 — HV / LV MAIN DISTRIBUTION
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
2.1 — HV INCOMING SUPPLY & TRANSFORMER (DEWA-coordinated)
2.1.1 | DEWA HV incoming service connection (RMU / package substation, supplied & installed by DEWA). Contractor allowance for coordination, application, attendance and acceptance. | P-200 (SLD) / P-300 (LV room) | Lot | 1 | 0 |  | 📋 DEWA-listed
2.1.2 | HV / LV distribution transformer — 2000 kVA, 11 kV / 0.4 kV, 50 Hz, vector group Dyn11, K-Factor rating ≥ K-13 (suitable for non-linear loads — LED lighting, EV chargers, VFDs; uplift to K-20 if EV load > 20 % of MD), cast-resin (dry-type) construction with encapsulated F-class windings, IP31 enclosure, anti-vibration mounts, ±2.5 % / ±5 % off-circuit tap changer, oil-free, low-loss DEWA-listed manufacturer. Sized for Building MD ~? kW + 25 % spare. Includes installation, energising, witnessed routine test, commissioning report. | P-200 (SLD) / P-300 (LV room) | Nr | 1 | 240000 |  | 📋 Schneider / ABB / Siemens / Trafo Union
2.1.3 | 11 kV HV cable (single-core 3×1C, XLPE/CWS/PVC, copper screen) from RMU to transformer HV side — complete with stress cones, heat-shrink terminations, fire stopping at penetrations, earthing, ID phase markers. | P-200 (SLD) / P-300 (LV room) | m | 30 | 18000 |  | 📋 — (contractor selection)
2.1.4 | Transformer room civil / MEP coordination — pressure-relief vents, mechanical ventilation, drainage, fire-rated enclosure (≥ 2 h), DEWA-spec oil bund where oil-filled (N/A for cast-resin) — coordination only. | P-200 (SLD) / P-300 (LV room) | Sum | 1 | 35000 |  | 📋 Schneider / ABB / Siemens / Trafo Union
Sub-Total 2.1
2.2 — LV PANELS (Supply, Install, Test & Commission)
2.2.1 | Main LV Panel — sized per Maximum Demand. Supply, install, test, commission complete with ACB, busbars, MCCBs as per SLD. | P-200 (SLD) / P-300 (LV room) | Nr | 1 |  |  | 📐 Coordinate with consultant
Sub-Total 2.2
2.3 — STANDBY GENERATOR & ATS
2.3.1 | Standby generator + ATS — sized per essential-load schedule. Supply, install, commission complete. | P-200 (SLD) / P-300 (LV room) | Set | 1 | 80000 |  | 📐 Cummins / Caterpillar / FG Wilson / Perkins
Sub-Total 2.3
BILL 2 — TOTAL CARRIED TO SUMMARY

## Bill 3 - SMDBs
BILL No. 3 — SUB-MAIN DISTRIBUTION BOARDS (SMDBS)
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
3.1 — TYPICAL FLOOR SMDBs (1F–8F)
3.1.1 | SMDB-1F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-103 (1F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.1.2 | SMDB-2F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-104 (2F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.1.3 | SMDB-3F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-105 (3F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.1.4 | SMDB-4F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-104 (4F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.1.5 | SMDB-5F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-105 (5F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.1.6 | SMDB-6F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-104 (6F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.1.7 | SMDB-7F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-105 (7F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.1.8 | SMDB-8F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-104 (8F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
Sub-Total 3.1
3.2 — GROUND FLOOR SMDBs
3.2.1 | SMDB-G: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 125A TP MCCB ≥35 kA Icu incomer, busbar 125 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 60.55 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-102 (Ground) | Nr | 1 | 14000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.2 | SMDB-SH01: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.3 | SMDB-SH02: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.4 | SMDB-SH03: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.5 | SMDB-SH04: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.6 | SMDB-SH05: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 25 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.7 | SMDB-SH06: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.8 | SMDB-SH07: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.9 | SMDB-SH08: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 40 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.10 | SMDB-SH09: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.11 | SMDB-SH10: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.12 | SMDB-SH11: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.2.13 | SMDB-SH12: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 63A TP MCCB ≥35 kA Icu incomer, busbar 63 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 30 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 9000 |  | 📐 Schneider / Hager / Legrand / ABB
Sub-Total 3.2
3.3 — ROOF SMDBs
3.3.1 | SMDB-RF: floor-standing SMDB, IP65 stainless-steel 316L weatherproof enclosure with UV-resistant gland kits and sun-shield canopy, 415 V / 3P+N+E, 500A TP MCCB ≥35 kA Icu incomer, busbar 500 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 248.63 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-106 (Roof) | Nr | 1 | 79200 |  | 📐 Schneider / Hager / Legrand / ABB
Sub-Total 3.3
3.4 — SPECIAL-DUTY SMDBs (EV / Lift / etc.)
3.4.1 | SMDB-EV: wall-mounted SMDB, IP54 powder-coated mild-steel enclosure (epoxy-polyester finish), splash + dust-protected, 415 V / 3P+N+E, 160A TP MCCB ≥35 kA Icu incomer, busbar 160 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 88 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-101 (Basement) | Nr | 1 | 16520 |  | 📐 Schneider / Hager / Legrand / ABB
Sub-Total 3.4
3.5 — RETAIL SMDBs
3.5.1 | SMDB-SH01: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.2 | SMDB-SH02: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.3 | SMDB-SH03: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.4 | SMDB-SH04: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.5 | SMDB-SH05: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 25 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.6 | SMDB-SH06: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.7 | SMDB-SH07: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.8 | SMDB-SH08: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 40 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.9 | SMDB-SH09: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.10 | SMDB-SH10: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.11 | SMDB-SH11: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.5.12 | SMDB-SH12: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 63A TP MCCB ≥35 kA Icu incomer, busbar 63 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 30 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 9000 |  | 📐 Schneider / Hager / Legrand / ABB
Sub-Total 3.5
3.6 — EMERGENCY SMDBs (Generator-backed, FR)
3.6.1 | SMDB-1F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-103 (1F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.2 | SMDB-2F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-104 (2F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.3 | SMDB-3F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-105 (3F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.4 | SMDB-4F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-104 (4F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.5 | SMDB-5F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-105 (5F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.6 | SMDB-6F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-104 (6F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.7 | SMDB-7F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-105 (7F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.8 | SMDB-8F: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 300A TP MCCB ≥35 kA Icu incomer, busbar 300 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 150.86 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-104 (8F) | Nr | 1 | 32000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.9 | SMDB-RF: floor-standing SMDB, IP65 stainless-steel 316L weatherproof enclosure with UV-resistant gland kits and sun-shield canopy, 415 V / 3P+N+E, 500A TP MCCB ≥35 kA Icu incomer, busbar 500 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 248.63 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-106 (Roof) | Nr | 1 | 79200 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.10 | SMDB-G: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 125A TP MCCB ≥35 kA Icu incomer, busbar 125 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 60.55 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-102 (Ground) | Nr | 1 | 14000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.11 | SMDB-EV: wall-mounted SMDB, IP54 powder-coated mild-steel enclosure (epoxy-polyester finish), splash + dust-protected, 415 V / 3P+N+E, 160A TP MCCB ≥35 kA Icu incomer, busbar 160 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 88 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-101 (Basement) | Nr | 1 | 16520 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.12 | SMDB-SH01: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.13 | SMDB-SH02: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.14 | SMDB-SH03: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.15 | SMDB-SH04: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.16 | SMDB-SH05: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 25 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.17 | SMDB-SH06: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.18 | SMDB-SH07: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.19 | SMDB-SH08: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 40 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.20 | SMDB-SH09: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 10 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.21 | SMDB-SH10: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.22 | SMDB-SH11: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 40A TP MCCB ≥35 kA Icu incomer, busbar 40 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 15 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.23 | SMDB-SH12: wall-mounted SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 63A TP MCCB ≥35 kA Icu incomer, busbar 63 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 30 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) | Nr | 1 | 9000 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.24 | ESMDB-G: floor-standing SMDB, IP31 powder-coated mild-steel enclosure with padlockable hinged door, 415 V / 3P+N+E, 400A TP MCCB ≥35 kA Icu incomer, busbar 400 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 190.08 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-102 (Ground) | Nr | 1 | 36800 |  | 📐 Schneider / Hager / Legrand / ABB
3.6.25 | ESMDB-RF: wall-mounted SMDB, IP65 stainless-steel 316L weatherproof enclosure with UV-resistant gland kits and sun-shield canopy, 415 V / 3P+N+E, 160A TP MCCB ≥35 kA Icu incomer, busbar 160 A Cu electro-tin plated, Form 2b separation, neutral / earth bars, outgoing MCCBs / MCBs / RCBOs as per SLD, MEB sub-bar bonded to building MEB, ID-engraved circuit labels, padlockable hinged door, manufacturer's factory acceptance test (FAT) certificate. Fire-rated cable glands + LSZH gland-kits at all FR feeder terminations. Connected load 88.69 kW. Supply, install, terminate, energise, witnessed routine test. | P-201 (SLD) / P-106 (Roof) | Nr | 1 | 26565 |  | 📐 Schneider / Hager / Legrand / ABB
Sub-Total 3.6
BILL 3 — TOTAL CARRIED TO SUMMARY

## Bill 4 - Distribution Boards
BILL No. 4 — DISTRIBUTION BOARDS (DBS) & CONSUMER UNITS
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
4.1 — DISTRIBUTION BOARDS (per cable schedule)
4.1.1 | DB-G: DB fed from SMDB-G, 63A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 9000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.2 | DB-F1: DB fed from SMDB-G, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.3 | DB-F4: DB fed from SMDB-G, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.4 | DB-F5: DB fed from SMDB-G, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.5 | DB-L.GYM: DB fed from SMDB-RF, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-106 (Roof) / P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.6 | DB-G.GYM: DB fed from SMDB-RF, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-106 (Roof) / P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.7 | DB-WM: DB fed from SMDB-RF, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-106 (Roof) / P-201 (SLD) | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.8 | EDB-G: DB fed from ESMDB-G, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (Emergency) / Floor plan | Nr | 1 | 6900 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.9 | EDB-1F: DB fed from ESMDB-G, 32A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (Emergency) / Floor plan | Nr | 1 | 6900 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.10 | EDB-TEL: DB fed from ESMDB-G, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (Emergency) / Floor plan | Nr | 1 | 6900 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.11 | EDB-PR: DB fed from ESMDB-G, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (Emergency) / Floor plan | Nr | 1 | 6900 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.12 | EDB-4F: DB fed from ESMDB-RF, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-106 (Roof) / P-201 (SLD) | Nr | 1 | 6900 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.13 | EDB-7F: DB fed from ESMDB-RF, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-106 (Roof) / P-201 (SLD) | Nr | 1 | 6900 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.14 | EDB-GSM-R: DB fed from ESMDB-RF, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-106 (Roof) / P-201 (SLD) | Nr | 1 | 6900 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.15 | DB-T1 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.16 | DB-T2 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.17 | DB-T3 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.18 | DB-T4 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.19 | DB-T5 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.20 | DB-T6 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.21 | DB-T7 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.22 | DB-T8 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.23 | DB-T9 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.24 | DB-T10 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.25 | DB-T11 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.26 | DB-T12 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.27 | DB-T13 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.28 | DB-T14 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.29 | DB-T15 (odd floors): DB fed from SMDB-TF-odd, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.30 | DB-T1 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.31 | DB-T2 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.32 | DB-T3 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.33 | DB-T4 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.34 | DB-T5 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.35 | DB-T6 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.36 | DB-T7 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.37 | DB-T8 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.38 | DB-T9 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.39 | DB-T10 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.40 | DB-T11 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.41 | DB-T12 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.42 | DB-T13 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.43 | DB-T14 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.44 | DB-T15 (even floors): DB fed from SMDB-TF-even, 40A TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 6000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.45 | DB-SHOP1: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.46 | DB-SHOP2: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.47 | DB-SHOP3: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.48 | DB-SHOP4: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.49 | DB-SHOP5: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.50 | DB-SHOP6: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.51 | DB-SHOP7: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.52 | DB-SHOP8: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.53 | DB-SHOP9: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.54 | DB-SHOP10: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.55 | DB-SHOP11: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
4.1.56 | DB-SHOP12: DB fed from SMDB-SH01 to SMDB-SH12, TP incomer, IP4X. Supply, install, terminate, label, test & commission. | P-201 (SLD) / Floor plan | Nr | 1 | 12000 |  | 📐 Schneider / Hager / Legrand / ABB
Sub-Total 4.1
BILL 4 — TOTAL CARRIED TO SUMMARY

## Bill 5 - LV Cables
BILL No. 5 — LV POWER CABLES (Main + Distribution + Final Circuits)
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Cable Size | Description (Route & Scope) | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
5.1 — XLPE / SWA / PVC LV CABLES — Plant & Utility Risers (LV Panel → SMDB)
Spec (all rows in this section): XLPE / SWA / PVC 600/1000 V armoured cable to BS 5467 / IEC 60502, on plant / utility risers (non-public-area, non-escape-route). Installed in cable tray / ladder / conduit incl. fire stopping at penetrations, BW-type brass glands with shrouds, compression lugs, ferrules and terminations at both ends.
5.1.1 | 4C×150mm² XLPE/SWA/PVC | LVP-01 → SMDB-1F — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 25 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.2 | 4C×150mm² XLPE/SWA/PVC | LVP-01 → SMDB-2F — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 29 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.3 | 4C×150mm² XLPE/SWA/PVC | LVP-01 → SMDB-3F — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 33 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.4 | 4C×150mm² XLPE/SWA/PVC | LVP-01 → SMDB-4F — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 37 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.5 | 4C×150mm² XLPE/SWA/PVC | LVP-01 → SMDB-5F — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 41 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.6 | 4C×150mm² XLPE/SWA/PVC | LVP-01 → SMDB-6F — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 45 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.7 | 4C×150mm² XLPE/SWA/PVC | LVP-01 → SMDB-7F — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 49 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.8 | 4C×150mm² XLPE/SWA/PVC | LVP-01 → SMDB-8F — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 53 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.9 | 4C×150mm² XLPE/SWA/PVC | LVP-02 → SMDB-RF — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 65 | 195 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.10 | 4C×50mm² XLPE/SWA/PVC | LVP-02 → SMDB-G — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 15 | 85 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.11 | 4C×70mm² XLPE/SWA/PVC | LVP-02 → SMDB-EV — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 20 | 110 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.12 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH01 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 20 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.13 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH02 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 22 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.14 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH03 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 24 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.15 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH04 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 26 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.16 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH05 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 28 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.17 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH06 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 30 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.18 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH07 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 32 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.19 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH08 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 34 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.20 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH09 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 36 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.21 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH10 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 38 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.22 | 4C×10mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH11 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 40 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.1.23 | 4C×16mm² XLPE/SWA/PVC | LVP-02 → SMDB-SH12 — plant / utility riser | P-200 (SLD) / P-010 (Cable tray) | m | 42 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
Sub-Total 5.1
5.2 — FIRE-RATED LSZH CABLES (BS 6387 CWZ / IEC 60331-21 — life-safety circuits)
Spec (all rows in this section): Fire-Rated LSZH cable to BS 6387 CWZ / IEC 60331-21 (950 °C / 3 h circuit integrity); LSZH outer jacket per BS 7211 / IEC 60332-3 Cat C / IEC 61034 / IEC 60754. Dedicated fire-rated containment, FR cleats at max 300 mm centres, FR/LSZH glands, FR terminations, red ID labels.
5.2.1 | 4C×70mm² FR/LSZH | LVP-02 → ESMDB-G — life-safety circuit | P-200 (SLD) / P-010 (Cable tray) | m | 15 | 229 |  | 📐 Ducab FR / Pirelli / Prysmian / Nexans
5.2.2 | 4C×185mm² FR/LSZH | LVP-02 → Fire Pump — life-safety circuit | P-200 (SLD) / P-010 (Cable tray) | m | 35 | 510 |  | 📐 Ducab FR / Pirelli / Prysmian / Nexans
Sub-Total 5.2
5.3 — DISTRIBUTION CABLES (SMDB → DB) — XLPE / SWA / PVC
Spec (all rows in this section): XLPE / SWA / PVC 600/1000 V armoured cable to BS 5467 / IEC 60502, on plant / utility risers (non-public-area, non-escape-route). Installed in cable tray / ladder / conduit incl. fire stopping at penetrations, BW-type brass glands with shrouds, compression lugs, ferrules and terminations at both ends.
5.3.1 | 4C×16mm² XLPE/SWA/PVC | SMDB-G → DB-G — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 20 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.2 | 4C×10mm² XLPE/SWA/PVC | SMDB-G → DB-F1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 15 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.3 | 4C×10mm² XLPE/SWA/PVC | SMDB-G → DB-F4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 15 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.4 | 4C×10mm² XLPE/SWA/PVC | SMDB-G → DB-F5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 15 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.5 | 4C×10mm² XLPE/SWA/PVC | SMDB-RF → DB-L.GYM — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 20 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.6 | 4C×10mm² XLPE/SWA/PVC | SMDB-RF → DB-G.GYM — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 20 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.7 | 4C×10mm² XLPE/SWA/PVC | SMDB-RF → DB-WM — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 15 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.8 | 4C×10mm² XLPE/SWA/PVC | ESMDB-G → EDB-G — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 15 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.9 | 4C×6mm² XLPE/SWA/PVC | ESMDB-G → EDB-1F — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 14 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.10 | 4C×10mm² XLPE/SWA/PVC | ESMDB-G → EDB-TEL — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 15 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.11 | 4C×10mm² XLPE/SWA/PVC | ESMDB-G → EDB-PR — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 30 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.12 | 4C×10mm² XLPE/SWA/PVC | ESMDB-RF → EDB-4F — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 20 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.13 | 4C×10mm² XLPE/SWA/PVC | ESMDB-RF → EDB-7F — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 10 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.14 | 4C×10mm² XLPE/SWA/PVC | ESMDB-RF → EDB-GSM-R — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 15 | 22 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.15 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.16 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T2 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.17 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T3 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.18 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.19 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.20 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T6 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.21 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T7 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.22 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T8 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.23 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T9 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.24 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T10 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.25 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T11 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.26 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T12 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.27 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T13 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.28 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T14 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.29 | 4C×16mm² XLPE/SWA/PVC | SMDB-1F → DB-T15 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.30 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.31 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T2 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.32 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T3 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.33 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.34 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.35 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T6 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.36 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T7 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.37 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T8 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.38 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T9 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.39 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T10 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.40 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T11 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.41 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T12 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.42 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T13 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.43 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T14 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.44 | 4C×16mm² XLPE/SWA/PVC | SMDB-3F → DB-T15 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.45 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.46 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T2 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.47 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T3 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.48 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.49 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.50 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T6 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.51 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T7 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.52 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T8 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.53 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T9 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.54 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T10 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.55 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T11 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.56 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T12 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.57 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T13 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.58 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T14 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.59 | 4C×16mm² XLPE/SWA/PVC | SMDB-5F → DB-T15 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.60 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.61 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T2 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.62 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T3 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.63 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.64 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.65 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T6 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.66 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T7 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.67 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T8 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.68 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T9 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.69 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T10 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.70 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T11 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.71 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T12 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.72 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T13 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.73 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T14 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.74 | 4C×16mm² XLPE/SWA/PVC | SMDB-7F → DB-T15 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.75 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.76 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T2 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.77 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T3 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.78 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.79 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.80 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T6 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.81 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T7 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.82 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T8 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.83 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T9 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.84 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T10 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.85 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T11 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.86 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T12 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.87 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T13 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.88 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T14 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.89 | 4C×16mm² XLPE/SWA/PVC | SMDB-2F → DB-T15 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.90 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.91 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T2 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.92 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T3 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.93 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.94 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.95 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T6 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.96 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T7 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.97 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T8 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.98 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T9 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.99 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T10 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.100 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T11 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.101 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T12 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.102 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T13 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.103 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T14 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.104 | 4C×16mm² XLPE/SWA/PVC | SMDB-4F → DB-T15 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.105 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.106 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T2 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.107 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T3 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.108 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.109 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.110 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T6 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.111 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T7 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.112 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T8 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.113 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T9 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.114 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T10 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.115 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T11 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.116 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T12 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.117 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T13 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.118 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T14 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.119 | 4C×16mm² XLPE/SWA/PVC | SMDB-6F → DB-T15 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.120 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T1 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.121 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T2 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.122 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T3 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.123 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T4 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.124 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T5 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.125 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T6 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.126 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T7 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.127 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T8 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.128 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T9 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.129 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T10 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.130 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T11 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.131 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T12 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.132 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T13 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.133 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T14 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
5.3.134 | 4C×16mm² XLPE/SWA/PVC | SMDB-8F → DB-T15 — SMDB → DB distribution | P-201 (SLD) / Floor plan | m | 25 | 32 |  | 📐 Ducab / NCC / Oman Cables / Riyadh Cables
Sub-Total 5.3
5.5 — LSZH CABLES — Public-Area & Escape-Route Final Circuits (DCD compliance)
5.5.1 | LSZH 4C × 16 mm² | Corridor & lobby final-circuit risers, escape-route mains (BS 7211 / IEC 60332-3 Cat C / IEC 61034 / IEC 60754). | P-103 … P-108 / P-201 | m | 220 | 42 |  | 📋 Ducab LSZH / Prysmian / Helkama / Nexans
5.5.2 | LSZH 3C × 4 mm² Cu | Apartment lighting & socket sub-mains in escape corridors. | P-103 … P-108 / P-201 | m | 480 | 11 |  | 📋 Ducab LSZH / Prysmian / Helkama / Nexans
5.5.3 | LSZH 3C × 2.5 mm² Cu | Final-circuit drops to apartment outlets & accessories on escape route. | P-103 … P-108 / P-201 | m | 1200 | 8 |  | 📋 Ducab LSZH / Prysmian / Helkama / Nexans
5.5.4 | LSZH 2C × 1.5 mm² Cu | Emergency / exit-sign final circuits (combined with FR per Bill 5.2). | P-103 … P-108 / P-201 | m | 540 | 7 |  | 📋 Ducab FR / Pirelli / Prysmian / Nexans
Sub-Total 5.5
5.7 — EARTH CONTINUITY CONDUCTORS (ECC) ALONGSIDE RISING MAINS
5.7.1 | 1C × 35 mm² G/Y XLPE ECC | Alongside fire-rated rising mains (allowance). | P-200 (SLD) / BS 6004 | m | 50 | 27 |  | 📋 Ducab FR / Pirelli / Prysmian / Nexans
5.7.2 | 1C × 10–70 mm² G/Y XLPE ECC | Alongside XLPE rising mains (allow per run). | P-200 (SLD) / BS 6004 | m | 709 | 30 |  | 📋 Ducab / NCC / Oman Cables / Riyadh Cables
Sub-Total 5.7
BILL 5 — TOTAL CARRIED TO SUMMARY

## Bill 6 - Containment
BILL No. 6 — CABLE CONTAINMENT (TRAY, LADDER, TRUNKING, CONDUIT)
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
6.1 — CABLE TRAYS, LADDERS, TRUNKING & CONDUITS
6.1.1 | 300mm wide HDGI cable tray — LV room + main vertical risers, hot-dip galvanised to BS EN ISO 1461, c/w supports at max 1.5m centres on horizontal / 1.0m on vertical, brackets, bends, tees, reducers, copplers, fixings, earth bonding straps. | P-010 (Cable tray detail) / P-201 | m | 180 | 385 |  | 📋 Marshall Tufflex / Vergokan / Niedax / Eltete
6.1.2 | 150mm wide HDGI cable tray — SMDB to DB horizontal distribution, hot-dip galvanised to BS EN ISO 1461, c/w supports at max 1.5m centres on horizontal / 1.0m on vertical, brackets, bends, tees, reducers, copplers, fixings, earth bonding straps. | P-010 (Cable tray detail) / P-201 | m | 320 | 195 |  | 📋 Marshall Tufflex / Vergokan / Niedax / Eltete
6.1.3 | 100mm wide HDGI cable tray — branch distribution, hot-dip galvanised to BS EN ISO 1461, c/w supports at max 1.5m centres on horizontal / 1.0m on vertical, brackets, bends, tees, reducers, copplers, fixings, earth bonding straps. | P-010 (Cable tray detail) / P-201 | m | 250 | 160 |  | 📋 Marshall Tufflex / Vergokan / Niedax / Eltete
6.1.4 | 100×100mm GI trunking — riser shafts, hot-dip galvanised to BS EN ISO 1461, c/w supports at max 1.5m centres on horizontal / 1.0m on vertical, brackets, bends, tees, reducers, copplers, fixings, earth bonding straps. | P-010 (Cable tray detail) / P-201 | m | 120 | 160 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
6.1.5 | Ø25mm GI conduit — exposed / mechanical equipment & wet areas, hot-dip galvanised to BS EN ISO 1461, c/w supports at max 1.5m centres on horizontal / 1.0m on vertical, brackets, bends, tees, reducers, copplers, fixings, earth bonding straps. | P-010 (Cable tray detail) / P-201 | m | 600 | 48 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
6.1.6 | Ø25mm PVC conduit — concealed sub-mains, hot-dip galvanised to BS EN ISO 1461, c/w supports at max 1.5m centres on horizontal / 1.0m on vertical, brackets, bends, tees, reducers, copplers, fixings, earth bonding straps. | P-010 (Cable tray detail) / P-201 | m | 2800 | 48 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
6.1.7 | Ø20mm PVC conduit — concealed final circuits to outlets & lighting points, hot-dip galvanised to BS EN ISO 1461, c/w supports at max 1.5m centres on horizontal / 1.0m on vertical, brackets, bends, tees, reducers, copplers, fixings, earth bonding straps. | P-010 (Cable tray detail) / P-201 | m | 9000 | 48 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
6.1.8 | Pull boxes at every 15m of conduit run or two 90° bends (General Note 14), hot-dip galvanised to BS EN ISO 1461, c/w supports at max 1.5m centres on horizontal / 1.0m on vertical, brackets, bends, tees, reducers, copplers, fixings, earth bonding straps. | P-010 (Cable tray detail) / P-201 | Nr | 400 | 24 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
Sub-Total 6.1
BILL 6 — TOTAL CARRIED TO SUMMARY

## Bill 7 - Wiring Devices
BILL No. 7 — WIRING DEVICES & ACCESSORIES
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
7.1 — BASEMENT — SOCKET OUTLETS & SMALL POWER
7.1.1 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 40 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.1.2 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 16 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.1.3 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 6 | 85 |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.1 — Basement
7.2 — GROUND FLOOR — SOCKET OUTLETS & SMALL POWER
7.2.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 40 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.2.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 28 |  |  | 📋 MK / Schneider / Legrand / Hager
7.2.3 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 20 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.2.4 | Floor box — 13A twin socket + RJ45 dual outlet | P-103 … P-108 (Floor plans) | Nr | 18 | 75 |  | 📋 MK / Schneider / Legrand / Hager
7.2.5 | 13A flex outlet for hand dryer (common WCs) | P-103 … P-108 (Floor plans) | Nr | 8 |  |  | 📋 MK / Schneider / Legrand / Hager
7.2.6 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 6 | 45 |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.2 — Ground Floor
7.3 — 1F — SOCKET OUTLETS & SMALL POWER
7.3.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 88 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.3.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 162 |  |  | 📋 MK / Schneider / Legrand / Hager
7.3.3 | 13A 230V twin switched socket outlet + USB-A/USB-C ports | P-103 … P-108 (Floor plans) | Nr | 30 | 180 |  | 📋 MK / Schneider / Legrand / Hager
7.3.4 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.3.5 | 20A 230V flex outlet for water heater (with neon) | P-103 … P-108 (Floor plans) | Nr | 22 |  |  | 📋 MK / Schneider / Legrand / Hager
7.3.6 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 30 | 85 |  | 📋 MK / Schneider / Legrand / Hager
7.3.7 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 48 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.3.8 | 13A flex outlet for gas hob / cooker point | P-103 … P-108 (Floor plans) | Nr | 15 |  |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.3 — 1F
7.4 — 2F — SOCKET OUTLETS & SMALL POWER
7.4.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 88 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.4.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 162 |  |  | 📋 MK / Schneider / Legrand / Hager
7.4.3 | 13A 230V twin switched socket outlet + USB-A/USB-C ports | P-103 … P-108 (Floor plans) | Nr | 30 | 180 |  | 📋 MK / Schneider / Legrand / Hager
7.4.4 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.4.5 | 20A 230V flex outlet for water heater (with neon) | P-103 … P-108 (Floor plans) | Nr | 22 |  |  | 📋 MK / Schneider / Legrand / Hager
7.4.6 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 30 | 85 |  | 📋 MK / Schneider / Legrand / Hager
7.4.7 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 48 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.4.8 | 13A flex outlet for gas hob / cooker point | P-103 … P-108 (Floor plans) | Nr | 15 |  |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.4 — 2F
7.5 — 3F — SOCKET OUTLETS & SMALL POWER
7.5.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 88 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.5.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 162 |  |  | 📋 MK / Schneider / Legrand / Hager
7.5.3 | 13A 230V twin switched socket outlet + USB-A/USB-C ports | P-103 … P-108 (Floor plans) | Nr | 30 | 180 |  | 📋 MK / Schneider / Legrand / Hager
7.5.4 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.5.5 | 20A 230V flex outlet for water heater (with neon) | P-103 … P-108 (Floor plans) | Nr | 22 |  |  | 📋 MK / Schneider / Legrand / Hager
7.5.6 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 30 | 85 |  | 📋 MK / Schneider / Legrand / Hager
7.5.7 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 48 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.5.8 | 13A flex outlet for gas hob / cooker point | P-103 … P-108 (Floor plans) | Nr | 15 |  |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.5 — 3F
7.6 — 4F — SOCKET OUTLETS & SMALL POWER
7.6.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 88 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.6.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 162 |  |  | 📋 MK / Schneider / Legrand / Hager
7.6.3 | 13A 230V twin switched socket outlet + USB-A/USB-C ports | P-103 … P-108 (Floor plans) | Nr | 30 | 180 |  | 📋 MK / Schneider / Legrand / Hager
7.6.4 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.6.5 | 20A 230V flex outlet for water heater (with neon) | P-103 … P-108 (Floor plans) | Nr | 22 |  |  | 📋 MK / Schneider / Legrand / Hager
7.6.6 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 30 | 85 |  | 📋 MK / Schneider / Legrand / Hager
7.6.7 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 48 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.6.8 | 13A flex outlet for gas hob / cooker point | P-103 … P-108 (Floor plans) | Nr | 15 |  |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.6 — 4F
7.7 — 5F — SOCKET OUTLETS & SMALL POWER
7.7.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 88 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.7.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 162 |  |  | 📋 MK / Schneider / Legrand / Hager
7.7.3 | 13A 230V twin switched socket outlet + USB-A/USB-C ports | P-103 … P-108 (Floor plans) | Nr | 30 | 180 |  | 📋 MK / Schneider / Legrand / Hager
7.7.4 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.7.5 | 20A 230V flex outlet for water heater (with neon) | P-103 … P-108 (Floor plans) | Nr | 22 |  |  | 📋 MK / Schneider / Legrand / Hager
7.7.6 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 30 | 85 |  | 📋 MK / Schneider / Legrand / Hager
7.7.7 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 48 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.7.8 | 13A flex outlet for gas hob / cooker point | P-103 … P-108 (Floor plans) | Nr | 15 |  |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.7 — 5F
7.8 — 6F — SOCKET OUTLETS & SMALL POWER
7.8.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 88 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.8.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 162 |  |  | 📋 MK / Schneider / Legrand / Hager
7.8.3 | 13A 230V twin switched socket outlet + USB-A/USB-C ports | P-103 … P-108 (Floor plans) | Nr | 30 | 180 |  | 📋 MK / Schneider / Legrand / Hager
7.8.4 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.8.5 | 20A 230V flex outlet for water heater (with neon) | P-103 … P-108 (Floor plans) | Nr | 22 |  |  | 📋 MK / Schneider / Legrand / Hager
7.8.6 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 30 | 85 |  | 📋 MK / Schneider / Legrand / Hager
7.8.7 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 48 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.8.8 | 13A flex outlet for gas hob / cooker point | P-103 … P-108 (Floor plans) | Nr | 15 |  |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.8 — 6F
7.9 — 7F — SOCKET OUTLETS & SMALL POWER
7.9.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 88 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.9.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 162 |  |  | 📋 MK / Schneider / Legrand / Hager
7.9.3 | 13A 230V twin switched socket outlet + USB-A/USB-C ports | P-103 … P-108 (Floor plans) | Nr | 30 | 180 |  | 📋 MK / Schneider / Legrand / Hager
7.9.4 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.9.5 | 20A 230V flex outlet for water heater (with neon) | P-103 … P-108 (Floor plans) | Nr | 22 |  |  | 📋 MK / Schneider / Legrand / Hager
7.9.6 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 30 | 85 |  | 📋 MK / Schneider / Legrand / Hager
7.9.7 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 48 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.9.8 | 13A flex outlet for gas hob / cooker point | P-103 … P-108 (Floor plans) | Nr | 15 |  |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.9 — 7F
7.10 — 8F — SOCKET OUTLETS & SMALL POWER
7.10.1 | 13A 230V SP switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 88 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.10.2 | 13A 230V twin switched socket outlet (BS 1363) | P-103 … P-108 (Floor plans) | Nr | 162 |  |  | 📋 MK / Schneider / Legrand / Hager
7.10.3 | 13A 230V twin switched socket outlet + USB-A/USB-C ports | P-103 … P-108 (Floor plans) | Nr | 30 | 180 |  | 📋 MK / Schneider / Legrand / Hager
7.10.4 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.10.5 | 20A 230V flex outlet for water heater (with neon) | P-103 … P-108 (Floor plans) | Nr | 22 |  |  | 📋 MK / Schneider / Legrand / Hager
7.10.6 | 20A 230V DP switch — water heater / cooker isolation | P-103 … P-108 (Floor plans) | Nr | 30 | 85 |  | 📋 MK / Schneider / Legrand / Hager
7.10.7 | 13A switched fused spur with neon for FCU (AC indoor unit) | P-103 … P-108 (Floor plans) | Nr | 48 | 45 |  | 📋 MK / Schneider / Legrand / Hager
7.10.8 | 13A flex outlet for gas hob / cooker point | P-103 … P-108 (Floor plans) | Nr | 15 |  |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.10 — 8F
7.11 — ROOF — SOCKET OUTLETS & SMALL POWER
7.11.1 | 16A industrial socket outlet — BMU provision | P-103 … P-108 (Floor plans) | Nr | 6 |  |  | 📋 MK / Schneider / Legrand / Hager
7.11.2 | 13A 230V weatherproof IP55 socket outlet | P-103 … P-108 (Floor plans) | Nr | 20 | 95 |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.11 — Roof
7.12 — SWITCHES & CONTROLS
7.12.1 | 1-gang / 2-gang lighting switches, 10A 250V grid-style, white moulded plate (BS 3676) | P-103 … P-108 (Floor plans) | Nr | 520 | 25 |  | 📋 MK / Schneider / Legrand / Hager
7.12.2 | 2-way / intermediate switches (corridors, stairs) | P-103 … P-108 (Floor plans) | Nr | 45 | 30 |  | 📋 MK / Schneider / Legrand / Hager
7.12.3 | Dimmer switch, 1-gang, 250 W LED-compatible | P-103 … P-108 (Floor plans) | Nr | 60 | 120 |  | 📋 MK / Schneider / Legrand / Hager
7.12.4 | Occupancy / PIR sensor (corridors, BOH, stores), with manual override | P-103 … P-108 (Floor plans) | Nr | 30 | 95 |  | 📋 MK / Schneider / Legrand / Hager
7.12.5 | Doorbell push + chime kit (apartments) | P-103 … P-108 (Floor plans) | Set | 25 | 150 |  | 📋 MK / Schneider / Legrand / Hager
7.12.6 | Connection unit (FCU), 3 A fused, for ceiling/extract fans | P-103 … P-108 (Floor plans) | Nr | 75 | 60 |  | 📋 MK / Schneider / Legrand / Hager
Sub-Total 7.12
7.13 — ISOLATORS & EV CHARGER OUTLETS
7.13.1 | Isolator, 4P 32A, weatherproof IP55, for outdoor mech. equipment | P-103 … P-108 (Floor plans) | Nr | 22 | 125 |  | 📋 MK / Schneider / Legrand / Hager
7.13.2 | Isolator, 2P 20A, indoor IP20 — small fixed equipment | P-103 … P-108 (Floor plans) | Nr | 18 | 75 |  | 📋 MK / Schneider / Legrand / Hager
7.13.3 | EV charger socket outlet — 7 kW AC Mode 3 Type 2 (basement parking) | P-103 … P-108 (Floor plans) | Nr | 8 | 3500 |  | 📋 ABB Terra / Schneider / Wallbox / Delta
7.13.4 | EV charger socket outlet — 22 kW AC Mode 3 Type 2 (basement parking) | P-103 … P-108 (Floor plans) | Nr | 2 | 8500 |  | 📋 ABB Terra / Schneider / Wallbox / Delta
Sub-Total 7.13
BILL 7 — TOTAL CARRIED TO SUMMARY

## Bill 8 - Lighting Fixtures
BILL No. 8 — LIGHTING FIXTURES (INTERNAL + EXTERNAL)
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
8.0 — GENERIC ESTIMATE (no fixture legend read from drawings — review against ELV/lighting layout)
8.1 — INTERIOR LIGHTING — APARTMENTS & COMMON AREAS
8.1.1 | Recessed LED downlight, 12 W / 800 lm, 4000 K, IP20, anti-glare reflector (apartments, lobby, corridors) | P-103 … P-108 (Floor plans) | Nr | 480 | 85 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
8.1.2 | Surface-mount LED panel, 600×600 mm, 36 W / 3600 lm, 4000 K (lobby, BOH) | P-103 … P-108 (Floor plans) | Nr | 60 | 640 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
8.1.3 | Linear LED batten 1200 mm, 36 W / 4000 lm, 4000 K, IP40 (car park, services) | P-103 … P-108 (Floor plans) | Nr | 220 | 640 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
8.1.4 | Bulkhead LED fitting, 12 W, IP65, polycarbonate (staircase, plant rooms) | P-103 … P-108 (Floor plans) | Nr | 90 | 95 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
8.1.5 | Wall-mounted LED bracket light (corridors, accent) | P-103 … P-108 (Floor plans) | Nr | 65 | 150 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
8.1.6 | Pendant decorative LED fixture (lobby — provisional) | P-103 … P-108 (Floor plans) | Nr | 8 | 450 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
8.1.7 | Track lighting LED spot, 15 W, 3000 K (retail — provisional) | P-103 … P-108 (Floor plans) | Nr | 40 | 140 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
Sub-Total 8.1
8.2 — EXTERIOR LIGHTING (Façade, Podium, Parking)
8.2.1 | External wall-mounted LED fixture, 24 W, IP65, anti-glare optic (podium, façade) | P-100 (Site / external) | Nr | 36 | 280 |  | 📋 Philips Lumec / Disano / iGuzzini / Thorn
8.2.2 | Pole-mounted parking LED area light, 80 W, 4000 K, IP66, on 6 m pole | P-100 (Site / external) | Nr | 14 | 1800 |  | 📋 Philips Lumec / Disano / iGuzzini / Thorn
8.2.3 | Step / kerb LED light, 3 W, IP67, recessed | P-100 (Site / external) | Nr | 28 | 95 |  | 📋 Philips Lumec / Disano / iGuzzini / Thorn
8.2.4 | Bollard LED, 20 W, IP65, 800 mm height (landscape) | P-100 (Site / external) | Nr | 16 | 640 |  | 📋 Philips Lumec / Disano / iGuzzini / Thorn
8.2.5 | Façade LED linear / wall-grazer, IP66 (provisional sum) | P-100 (Site / external) | Sum | 1 | 85000 |  | 📋 Philips Lumec / Disano / iGuzzini / Thorn
Sub-Total 8.2
8.3 — LIGHTING CONTROLS
8.3.1 | Time-clock / astronomical timer for façade and external lighting | P-200 (SLD) / Lighting controls | Set | 1 | 85000 |  | 📋 Philips Lumec / Disano / iGuzzini / Thorn
8.3.2 | Photocell / daylight sensor for external circuits | P-200 (SLD) / Lighting controls | Nr | 4 | 250 |  | 📋 MK / Schneider / Legrand / Hager
8.3.3 | DALI/0-10V dimmer module for common-area lighting (provisional) | P-200 (SLD) / Lighting controls | Sum | 1 | 120 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
Sub-Total 8.3
BILL 8 — TOTAL CARRIED TO SUMMARY

## Bill 9 - Earthing & LP
BILL No. 9 — EARTHING & LIGHTNING PROTECTION
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
9.1 — MAIN EARTHING SYSTEM (TN-S, ≤ 1 Ω)
9.1.1 | Water-tight double-seal earth pit at basement level c/w 366mmØ seal tube, inspection chamber & low-resistance backfill (resistance test < 1 Ω) | P-300 (LV room) / P-001 (Notes) | Nr | 4 | 510 |  | 📋 Erico / Furse / DEHN / Pentair
9.1.2 | Copper earth rod 17.2mmØ × 3000mm solid copper (per earthing detail) | P-300 (LV room) / P-001 (Notes) | Nr | 4 | 48 |  | 📋 Erico / Furse / DEHN / Pentair
9.1.3 | 1C × 70mm² bare copper main earth conductor — earth pits to Main Earth Bar / DEWA earth terminal | P-300 (LV room) / P-001 (Notes) | m | 120 | 30 |  | 📋 Erico / Furse / DEHN / Pentair
9.1.4 | 1C × 25mm² G/Y earth conductor — MEB to SMDB sub-earth bars and risers | P-300 (LV room) / P-001 (Notes) | m | 350 | 13 |  | 📋 Erico / Furse / DEHN / Pentair
9.1.5 | 1C × 16mm² G/Y earth conductor — SMDB sub-bar to each DB plus cable-tray/trunking bonding | P-300 (LV room) / P-001 (Notes) | m | 800 | 9 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
9.1.6 | Main Earth Bar (MEB) 50×6mm copper busbar in LV room, drilled, insulated, labelled | P-300 (LV room) / P-001 (Notes) | Nr | 2 | 14 |  | 📋 Erico / Furse / DEHN / Pentair
9.1.7 | Surge Protection Device (SPD Type 1+2) at LV panel incomer | P-300 (LV room) / P-001 (Notes) | Nr | 2 | 4500 |  | 📋 DEHN / Erico / Furse / Helita
9.1.8 | Earth bonding of all steel equipment, trays, trunking & supports (per General Note 15/19) | P-300 (LV room) / P-001 (Notes) | Sum | 1 | 65 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
Sub-Total 9.1
9.2 — LIGHTNING PROTECTION (IEC 62305)
9.2.1 | Air termination — Franklin/ESE rod, copper-bonded, with insulator + fixing (rooftop) | P-100 (Site) / P-108 (Roof) | Nr | 6 | 1800 |  | 📋 DEHN / Erico / Furse / Helita
9.2.2 | Down conductor — 50mm² bare copper tape/wire, full building height (basement to roof) | P-100 (Site) / P-108 (Roof) | m | 240 | 85 |  | 📋 DEHN / Erico / Furse / Helita
9.2.3 | Test point chamber with disconnector, lockable lid, at base of each down conductor | P-100 (Site) / P-108 (Roof) | Nr | 4 | 1200 |  | 📋 DEHN / Erico / Furse / Helita
9.2.4 | Earth electrode for LP system — copper-bonded rod + inspection chamber | P-100 (Site) / P-108 (Roof) | Nr | 4 | 3500 |  | 📋 DEHN / Erico / Furse / Helita
9.2.5 | Surge protection device (SPD) Type 1+2 at LV panel main incomer | P-100 (Site) / P-108 (Roof) | Nr | 2 | 4500 |  | 📋 DEHN / Erico / Furse / Helita
9.2.6 | Lightning protection design certification, risk assessment per IEC 62305-2 | P-100 (Site) / P-108 (Roof) | Sum | 1 | 8000 |  | 📋 DEHN / Erico / Furse / Helita
9.2.7 | LP testing & DEWA acceptance certificate | P-100 (Site) / P-108 (Roof) | Sum | 1 | 6500 |  | 📋 DEHN / Erico / Furse / Helita
Sub-Total 9.2
BILL 9 — TOTAL CARRIED TO SUMMARY

## Bill 10 - Emergency Lighting
BILL No. 10 — EMERGENCY LIGHTING & LIFE SAFETY
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
10.1 — EMERGENCY LUMINAIRES (3-hour autonomy)
10.1.1 | Self-contained emergency LED downlight, 3 W, 3-hour duration, IP20, with self-test (corridors, lobbies) | P-103 … P-108 (Floor plans) / P-201 | Nr | 96 | 85 |  | 📋 Philips / Osram / Trilux / Thorn / Cooper
10.1.2 | Self-contained emergency bulkhead, 8 W, 3-hour, IP65 (staircase, plant rooms) | P-103 … P-108 (Floor plans) / P-201 | Nr | 48 | 380 |  | 📋 Chloride / Cooper / Tridonic / Hochiki
10.1.3 | Maintained emergency exit sign LED, single-sided, with arrow pictogram (BS EN 1838) | P-103 … P-108 (Floor plans) / P-201 | Nr | 64 | 320 |  | 📋 Chloride / Cooper / Tridonic / Hochiki
10.1.4 | Maintained emergency exit sign LED, double-sided, ceiling-mounted | P-103 … P-108 (Floor plans) / P-201 | Nr | 18 | 480 |  | 📋 Chloride / Cooper / Tridonic / Hochiki
Sub-Total 10.1
10.2 — EMERGENCY POWER FOR LIFE-SAFETY EQUIPMENT (FR feeders)
10.2.1 | Power supply for fire pump panel — Fire-Rated cable from ESMDB-RF, including isolator & terminations | P-200 (Essential) / P-201 (FR feeders) | Set | 1 | 13800 |  | 📋 MK / Schneider / Legrand / Hager
10.2.2 | Power supply for stair pressurisation fans — FR feeder & isolator | P-200 (Essential) / P-201 (FR feeders) | Set | 1 | 110 |  | 📋 MK / Schneider / Legrand / Hager
10.2.3 | Power supply for smoke-extract fans (basement & corridors) — FR feeder & isolator | P-200 (Essential) / P-201 (FR feeders) | Set | 1 | 110 |  | 📋 MK / Schneider / Legrand / Hager
10.2.4 | Power supply for sprinkler-system jockey pump & main pump motor starter | P-200 (Essential) / P-201 (FR feeders) | Set | 1 | 22000 |  | 📋
10.2.5 | Power supply for fire-fighter's lift (2-hour FR feeder) | P-200 (Essential) / P-201 (FR feeders) | Set | 1 | 28000 |  | 📋
Sub-Total 10.2
10.3 — CENTRAL BATTERY SYSTEM (CBS) — alternative to self-contained
10.3.1 | CBS cabinet — 24/48 V DC, 3-hour autonomy, sized for total emergency luminaire load (~8 kW for this project), VRLA sealed batteries, charger, supervision, BMS interface, IP31, lockable. Provisional sum. | P-201 (Emergency loop) / P-300 (CBS cabinet) | Sum | 1 | 85000 |  | 📋 Chloride / Cooper / Olympia / Hochiki
10.3.2 | Maintained-feed sub-circuits from CBS to corridor / public-area luminaires — Fire-Rated cable in dedicated FR containment, ID-labelled in red (allow per riser). | P-201 (Emergency loop) / P-300 (CBS cabinet) | m | 180 | 38 |  | 📋 Chloride / Cooper / Olympia / Hochiki
10.3.3 | CBS testing & 3-hour discharge witness test — under controlled outage, recording lumen output and battery voltage decay. | P-201 (Emergency loop) / P-300 (CBS cabinet) | Sum | 1 | 8500 |  | 📋
Sub-Total 10.3
10.4 — FIRE ALARM / MEP INTEGRATION (DCD requirement)
10.4.1 | Shunt-trip relay for FAHU isolation on Fire Alarm activation — 24 V DC monitored coil, status feedback to FACP, MCCB shunt-trip module. | Coordinate with FA contractor (FA-001 series) | Nr | 1 | 1800 |  | 📋 Schneider / ABB / Siemens / Eaton
10.4.2 | Shunt-trip relay for AHU isolation per air-handling zone — 24 V DC monitored, status feedback to FACP. (Allow per AHU zone — typical per floor) | Coordinate with FA contractor (FA-001 series) | Nr | 8 | 1800 |  | 📋 Schneider / ABB / Siemens / Eaton
10.4.3 | Lift fire-recall interface module — homes lifts to designated fire-recall floor on Fire Alarm signal, monitored by FACP. (Per lift bank) | Coordinate with FA contractor (FA-001 series) | Nr | 4 | 6500 |  | 📋 KONE / Otis / Schindler / Mitsubishi (lift OEM)
10.4.4 | Smoke / fire damper actuator power supply — 24 V DC monitored, with status feedback (allow per damper, including fire dampers and smoke control). | Coordinate with FA contractor (FA-001 series) | Nr | 24 | 1200 |  | 📋 Notifier / Honeywell / Edwards / Hochiki
10.4.5 | Mag-lock door release on fire alarm — fail-safe release, 24 V DC, monitored relay for FACP signalling. (Per access-controlled fire-route door.) | Coordinate with FA contractor (FA-001 series) | Nr | 12 | 950 |  | 📋 Notifier / Honeywell / Edwards / Hochiki
10.4.6 | FA-BMS interface relay rack — wall-mounted enclosure with 24 V DC PSU, monitored output relays for HVAC / lighting / lift signalling to FACP & BMS. | Coordinate with FA contractor (FA-001 series) | Set | 1 | 18000 |  | 📋 Notifier / Honeywell / Edwards / Hochiki
10.4.7 | FA system tie-in cabling — Fire-Rated 2-core control cable from FACP to interface relays / shunt-trips / damper actuators. (Allow per tie-in.) | Coordinate with FA contractor (FA-001 series) | m | 280 | 65 |  | 📋 Schneider / ABB / Siemens / Eaton
Sub-Total 10.4
BILL 10 — TOTAL CARRIED TO SUMMARY

## Bill 11 - ELV Containment
BILL No. 11 — ELV CONTAINMENT (TEL/DATA, CCTV, ACS, MATV, FA)
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
11.1 — ELV CONTAINMENT — PROVISIONAL (specialist trades)
11.1.1 | Telephone / data containment — uPVC conduit Ø 25 mm + draw wires from MDF/IDF to apartment outlets | P-010 / Specialist trade | m | 1200 | 48 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
11.1.2 | CCTV containment — uPVC conduit Ø 25 mm + draw wires + back-boxes to camera locations | P-010 / Specialist trade | m | 600 | 48 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
11.1.3 | Access Control containment — conduit + wiring trough at every controlled door | P-010 / Specialist trade | m | 350 | 14 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
11.1.4 | MATV / SMATV containment — conduit + draw wires, MDF to apartment TV points | P-010 / Specialist trade | m | 800 | 14 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
11.1.5 | Fire Alarm containment — fire-rated conduit Ø 25/32 mm at all loops, isolator points (specialist supply by FA contractor) | P-010 / Specialist trade | m | 900 | 99 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
11.1.6 | BMS field cabling containment — conduit + tray at every field-device location (specialist supply by BMS contractor) | P-010 / Specialist trade | m | 600 | 14 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
11.1.7 | Audio-Video / Door-entry containment — conduit + back-boxes | P-010 / Specialist trade | m | 250 | 14 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
11.1.8 | ELV main risers — 100×100 mm GI trunking with separators between systems | P-010 / Specialist trade | m | 80 | 160 |  | 📋 Marshall Tufflex / Pemsa / Atkore / DSS
Sub-Total 11.1
BILL 11 — TOTAL CARRIED TO SUMMARY

## Bill 12 - Metering
BILL No. 12 — METERING & MONITORING
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
12.1 — DEWA SMART METERING — Tenant & Landlord (AMI-ready, DEWA Smart Grid Programme)
12.1.1 | DEWA-approved smart kWh meter, single-phase, AMI-ready (PLC + RF mesh communication), bi-directional metering capability, Class 1 accuracy, sealed, IEC 62052-11 / IEC 62053-21 compliant — for apartment tenants. Includes anti-tamper detection, configurable load-profile recording, remote-read capability. | P-300 (LV room) / DEWA Smart Grid spec | Nr | 120 | 850 |  | 📋 Itron / Landis+Gyr / Iskra (DEWA-listed)
12.1.2 | DEWA-approved smart kWh meter, three-phase, CT-operated, AMI-ready, bi-directional with consumption + export channel for Shams Dubai net metering (where PV applicable), Class 0.5S accuracy, sealed, IEC 62053-22 — for retail / common services / landlord. | P-300 (LV room) / DEWA Smart Grid spec | Nr | 12 | 2400 |  | 📋 Itron / Landis+Gyr / Iskra (DEWA-listed)
12.1.3 | DEWA-approved smart meter cabinet — DEWA Service Connection Specifications compliant, modular, lockable, ventilated, IP31, with sealed access door for DEWA-only opening, RJ-45 / RS-485 communication ports. | P-300 (LV room) / DEWA Smart Grid spec | Nr | 8 | 3200 |  | 📋 Itron / Landis+Gyr / Iskra (DEWA-listed)
12.1.4 | Current transformers (CTs) for smart-meter feeders — Class 0.5S, 250/5 / 400/5 / 630/5 / 2000/5 ratios per panel schedule, sealed, with DEWA-approved label. | P-300 (LV room) / DEWA Smart Grid spec | Set | 1 | 12000 |  | 📋 Schneider PowerLogic / Janitza / Carlo Gavazzi
12.1.5 | AMI head-end / data-concentrator (PLC + RF mesh gateway) — coordination with DEWA where centralised concentrator is supplied by DEWA; provisional allowance for concentrator location, power supply, and back-haul cabling. | P-300 (LV room) / DEWA Smart Grid spec | Sum | 1 | 28000 |  | 📋 Itron / Landis+Gyr / Iskra (DEWA-listed)
Sub-Total 12.1
12.2 — PANEL METERING, BMS INTEGRATION & MDM COORDINATION
12.2.1 | Multi-function digital meter (MFM) on LV panel main incomer & outgoing feeders — V/I/P/Q/PF/THD measurement, MODBUS RTU/TCP communication, Class 0.5 accuracy. | P-300 (LV room) / DEWA Smart Grid spec | Nr | 12 | 2800 |  | 📋 Schneider PowerLogic / Janitza / Carlo Gavazzi
12.2.2 | Energy-monitoring software / SCADA package for panel-level metering — head-end software, dashboards, historical data logging — provisional sum. | P-300 (LV room) / DEWA Smart Grid spec | Sum | 1 | 85000 |  | 📋 Itron / Landis+Gyr / Iskra (DEWA-listed)
12.2.3 | DEWA MDM (Meter Data Management) integration — testing of meter-to-MDM connectivity, data validation, and acceptance per DEWA AMI specifications. Provisional sum. | P-300 (LV room) / DEWA Smart Grid spec | Sum | 1 | 25000 |  | 📋 Itron / Landis+Gyr / Iskra (DEWA-listed)
12.2.4 | Wiring, terminations, CT secondaries, communication cabling (RS-485 / Cat6) for panel-level + smart-meter system. | P-300 (LV room) / DEWA Smart Grid spec | Sum | 1 | 18000 |  | 📋 Itron / Landis+Gyr / Iskra (DEWA-listed)
12.2.5 | DEWA-witnessed meter sealing & acceptance — including AMI commissioning and remote-read verification. | P-300 (LV room) / DEWA Smart Grid spec | Sum | 1 | 12000 |  | 📋 Itron / Landis+Gyr / Iskra (DEWA-listed)
Sub-Total 12.2
BILL 12 — TOTAL CARRIED TO SUMMARY

## Bill 13 - Test & Commissioning
BILL No. 13 — TESTING, COMMISSIONING & DEWA APPROVAL
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25 ¦ Authority: DEWA (Dubai Electricity & Water Authority)
Item | Description | Reference | Unit | Qty | Rate (AED) | Amount (AED) | Origin / Brand
13.1 — ROUTINE ELECTRICAL TESTS (Pre-energisation)
13.1.1 | Insulation resistance testing of all LV cables — 500 V/1000 V Megger, full report. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 18000 |  | 📋 — (contractor selection)
13.1.2 | Continuity & polarity testing of all final circuits. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 12000 |  | 📋 — (contractor selection)
13.1.3 | Earth fault loop impedance testing at every distribution board. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 2400 |  | 📋 — (contractor selection)
13.1.4 | Phase rotation & balance testing at all 3-phase feeders. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 6500 |  | 📋 — (contractor selection)
13.1.5 | RCD testing at all RCD/RCBO-protected circuits. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 5500 |  | 📋 — (contractor selection)
Sub-Total 13.1
13.2 — SYSTEM COMMISSIONING (Energisation & Performance)
13.2.1 | ATS changeover testing — simulate mains failure, verify auto-switchover, full load test. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 80000 |  | 📋 ABB / Socomec / Cummins / GE
13.2.2 | Standby generator full-load test — including load bank (if required), 4-hour run, fuel consumption recording. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 28000 |  | 📋 Cummins / Caterpillar / FG Wilson / Perkins
13.2.3 | Power-factor correction verification — record PF before/after capacitor bank energisation, harmonic analysis. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 8500 |  | 📋 — (contractor selection)
13.2.4 | Earthing system resistance test (Megger DET) at every electrode and MEB. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 1200 |  | 📋 Erico / Furse / DEHN / Pentair
13.2.5 | Lightning protection continuity test, including down-conductor resistance. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 5500 |  | 📋 DEHN / Erico / Furse / Helita
13.2.6 | Emergency lighting 3-hour duration test under controlled outage. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 4500 |  | 📋 — (contractor selection)
Sub-Total 13.2
13.3 — AUTHORITY APPROVALS & AS-BUILT DOCUMENTATION
13.3.1 | DEWA Inspection Coordination — coordinating multiple DEWA inspection visits during construction (cable rough-in, panel termination, earthing, metering pre-energisation, energising, post-energisation), submission of inspection requests, attendance, and rectifications until each stage is signed off. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 35000 |  | 📋 DEWA / DM / DCD / RTA
13.3.2 | DEWA Final Approval & Energisation — application fees, witnessed routine test, meter sealing, energising-permit issue. Provisional sum. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 50000 |  | 📋 DEWA / DM / DCD / RTA
13.3.3 | Dubai Municipality (DM) electrical inspection clearance — coordination with DM inspectors, attendance, and rectifications until clearance is obtained for occupancy / completion certificate. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 18000 |  | 📋 DEWA / DM / DCD / RTA
13.3.4 | DCD (Dubai Civil Defence) electrical clearance for life-safety installations — emergency lighting witnessed test, fire-pump power-supply inspection, smoke-control fan circuit verification. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 22000 |  | 📋 DEWA / DM / DCD / RTA
13.3.5 | As-Built Drawings — Consultant Approval. As-Built drawings (AutoCAD .dwg + PDF, 4 hard-copy bound sets), submitted to consultant for review, revisions until approved and signed. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 28000 |  | 📋 DEWA / DM / DCD / RTA
13.3.6 | As-Built Drawings — DEWA Approval. As-Built submission to DEWA in DEWA-required format (specific layer / title-block / electronic file structure), revisions until approved and filed by DEWA. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 32000 |  | 📋 DEWA / DM / DCD / RTA
13.3.7 | Energising application & meter installation coordination with DEWA — preparing application package, submitting to DEWA, attendance at DEWA appointments. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 12000 |  | 📋 DEWA / DM / DCD / RTA
13.3.8 | Final commissioning report — bound, signed, indexed (5 hard copies + electronic PDF), including all routine-test results, manufacturer test certificates, witness signatures. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 22000 |  | 📋 DEWA / DM / DCD / RTA
13.3.9 | Operator training — 2 sessions of 4 hours each, including written training material in English (and Arabic where requested), covering operation, routine maintenance, and emergency response. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 8500 |  | 📋 DEWA / DM / DCD / RTA
13.3.10 | Witnessed handover walk-through with consultant & employer team — verifying every installation against As-Built, snag list, sign-off. | DEWA / DM / DCD / IEC 60364-6 | Sum | 1 | 4500 |  | 📋 DEWA / DM / DCD / RTA
Sub-Total 13.3
BILL 13 — TOTAL CARRIED TO SUMMARY

## Summary of Bills
BILL OF QUANTITIES — SUMMARY OF BILLS
Proposed B+G+8+R Commercial & Residential Building ¦ Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job FA_P379 / CRs B/010/25
Bill | Description | Sheet Ref | Bill Total (AED) | Notes
1 | General Items / Preliminaries | Bill 1 | 0 | Mob, insurance, submittals, As-Built
2 | HV / LV Main Distribution | Bill 2 | 0 | Transformer, MDB, generator, ATS, capacitors
3 | Sub-Main Distribution Boards | Bill 3 | 0 | Typical floor, GF, RF, EV, retail, emergency
4 | Distribution Boards & Consumer Units | Bill 4 | 0 | Apt, common, retail, emergency, mech
5 | LV Power Cables | Bill 5 | 0 | Main + distribution + final + ECC + FR
6 | Cable Containment | Bill 6 | 0 | Tray, ladder, conduit, trunking
7 | Wiring Devices & Accessories | Bill 7 | 0 | Sockets, switches, isolators, EV outlets
8 | Lighting Fixtures | Bill 8 | 0 | Internal, external, controls
9 | Earthing & Lightning Protection | Bill 9 | 0 | TN-S, electrodes, LP system
10 | Emergency Lighting & Life Safety | Bill 10 | 0 | Self-contained, exit signs, FR feeders
11 | ELV Containment | Bill 11 | 0 | Tel/Data/CCTV/ACS/MATV/FA conduit
12 | Metering & Monitoring | Bill 12 | 0 | Tenant + panel meters, BMS integration
13 | Testing, Commissioning & DEWA Approval | Bill 13 | 0 | Routine tests + system commissioning + DEWA
SUB-TOTAL OF BILLS (Bills 1–13) |  |  | 0
Provisional Sums adjustment (if any) |  |  | 0 | Editable — net adjustment
Day Works Schedule (per separate schedule) |  |  | 0 | Editable
Contingency (10%) — on Bills 1–13 |  |  | 0
Discount (if offered, enter as negative) |  |  | 0 | Editable
TOTAL TENDER PRICE — Excluding VAT |  |  | 0
VAT (5%) — UAE Federal Tax Authority |  |  | 0
GRAND TOTAL TENDER PRICE — Including VAT |  |  | 0
FORM OF TENDER
We, the undersigned, having examined the tender drawings, specifications, and bill of quantities, do hereby offer to execute the works for the sum stated above (Grand Total Tender Price including VAT).
Validity period: 90 days from tender submission date.
Construction period: as specified in the contract documents.
Defects Liability Period: 12 months from substantial completion / handover.
Authorised signatory: SABI Engineering & Contracting LLC
TRN: 100XXXXXXXXXXXXX
Signature & Stamp: ____________________________ Date: ____________