## Cover
BILL OF QUANTITIES
ELECTRICAL POWER DISTRIBUTION WORKS
Project | Proposed B+G+8+R Commercial & Residential Building
Owner | Qutaiba Ameen Abdal Kija
Plot No. | 6731315 — Al Barsha South Third, Dubai, UAE
Architect | Engr. Samer Mahmoud Ajami (Reg. 105181)
Structural | Engr. Mohamad Maher Myaser Jabban (Reg. 101079)
Consultant | Future Art Engineering Consultancy
Job No. | FA_P379 / CRs B/010/25
Drawing Ref | P-001 … P-300 (14 sheets, Power Layout)
Drawing Date | 16.01.2026
BOQ Date | 05/05/2026
Authority | DEWA (Dubai Electricity & Water Authority)
Status | PRICED (INDICATIVE) — Dubai 2026 market rates · review before submission
BUILDING ELECTRICAL LOAD
Total Connected Load (TCL) | 2117.06 kW
Demand Factor | 0.75
Maximum Demand (MD) | ~1597 kW
SUMMARY OF SECTIONS
Section | Description | Sheet Ref
A | LV Switchgear & Sub-Main Distribution Boards (SMDBs) | Sheet A
B | Distribution Boards (DBs) & Consumer Units | Sheet B
C | LV Power Cables — Main & Rising Mains | Sheet C
D | LV Power Cables — Distribution (SMDB to DB) | Sheet D
E | Cable Management — Trays, Ladders & Conduits | Sheet E
F | Earthing & Bonding | Sheet F
G | Sundries, Accessories & Testing/Commissioning | Sheet G
RECONCILIATION NOTES — corrections applied vs source data
• LVP-01 → SMDB-1F…8F risers sized at 4C × 150mm² (PDF wins; XLSX source had 300mm², which is oversized for the 256 A load).
• Fire-pump feeder sized at 1×4C 185mm² FR + 1C 95mm² ECC (PDF wins; XLSX source had 2×4C 300mm² FR, which is oversized for 167 A start).
• ESMDB-G feeder sized at 4C × 300mm² FR (XLSX wins; PDF source had a 70mm² value in section 4 vs 300mm² in section 8.7 — 70mm² is undersized by ~3× for the 338 A load).
• Building totals on Cover (TCL 2,117.06 kW · MD ~1,597 kW · DF 0.80) sourced from comparison PDF — no load_summary in live extraction.
• Rate column F populated with INDICATIVE Dubai 2026 rates from scripts/lib/dubai-2026-rates.mjs. Review and adjust to actual supplier quotations before tender submission.
STATUS: PRICED (INDICATIVE) — Dubai 2026 market rates · review before submission
NOTE: All quantities are ESTIMATED. Cable lengths include 10% routing allowance. Confirm all quantities before procurement.

## A - Switchgear & SMDBs
BILL OF QUANTITIES — SECTION A: LV SWITCHGEAR & SUB-MAIN DISTRIBUTION BOARDS
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25
Item | Description | Reference | Unit | Qty | Unit Rate (AED) | Amount (AED) | Remarks
A1 — LV PANELS & MAIN SWITCHGEAR (Supply, Install, Test & Commission)
A1.1 | LVP-01: 3P+N+E, 415V, 50Hz, floor-standing, metal-clad LV switchboard, incl. 2000A main ACB (50 kA), busbars, metering. Outgoing: 8× 300A TP to SMDB-1F..8F. Complete as per SLD. | P-200 / P-201 | Nr | 1 | 600000 |  | LVP-01 main panel
A1.2 | Capacitor Bank — 375 kVAR, 415V, automatic PF correction for LVP-01. | SLD | Nr | 1 | 78750 |  | LVP-01 PF correction
A1.3 | LVP-02: 3P+N+E, 415V, 50Hz, floor-standing, metal-clad LV switchboard, incl. 1600A main ACB (50 kA), busbars, metering. Outgoing: 1× 500A TP to SMDB-RF, 1× 160A TP to SMDB-EV, 1× 125A TP to SMDB-G, 12× 50A TP to SMDB-SH01..12, 1× 400A TP to ESMDB-G, 1× 350A TP to Fire Pump. Complete as per SLD. | P-200 / P-201 | Nr | 1 | 450000 |  | LVP-02 main panel
A1.4 | Capacitor Bank — 275 kVAR, 415V, automatic PF correction for LVP-02. | SLD | Nr | 1 | 57750 |  | LVP-02 PF correction
A1.5 | Automatic Transfer Switch (ATS) Panel — 415V, 400A, 4P. Complete with controls and interlocking. | SLD | Nr | 1 | 80000 |  | Mains/Gen changeover
A1.6 | Standby Generator — 300 kVA, 415V/3Ph/50Hz, diesel, weatherproof canopy, AMF panel, fuel tank, exhaust, anti-vibration mounts. Complete installed and commissioned. | SLD | Nr | 1 | 255000 |  | Backup to essential
Sub-Total A1
A2 — SUB-MAIN DISTRIBUTION BOARDS (SMDBs) — Typical Floors
A2.1 | SMDB-1F: Floor-standing SMDB, 300A TP MCCB 35kA incomer, 415V, outgoing MCCBs as per SLD. Incl. busbar, earth bar, DIN rail, metering provisions. Supply, install, test & commission. Connected load: 150.86 kW. | SLD | Nr | 1 | 32000 |  | 1F — 150.86 kW
A2.2 | SMDB-2F: Floor-standing SMDB, 300A TP MCCB 35kA incomer, 415V, outgoing MCCBs as per SLD. Incl. busbar, earth bar, DIN rail, metering provisions. Supply, install, test & commission. Connected load: 150.86 kW. | SLD | Nr | 1 | 32000 |  | 2F — 150.86 kW
A2.3 | SMDB-3F: Floor-standing SMDB, 300A TP MCCB 35kA incomer, 415V, outgoing MCCBs as per SLD. Incl. busbar, earth bar, DIN rail, metering provisions. Supply, install, test & commission. Connected load: 150.86 kW. | SLD | Nr | 1 | 32000 |  | 3F — 150.86 kW
A2.4 | SMDB-4F: Floor-standing SMDB, 300A TP MCCB 35kA incomer, 415V, outgoing MCCBs as per SLD. Incl. busbar, earth bar, DIN rail, metering provisions. Supply, install, test & commission. Connected load: 150.86 kW. | SLD | Nr | 1 | 32000 |  | 4F — 150.86 kW
A2.5 | SMDB-5F: Floor-standing SMDB, 300A TP MCCB 35kA incomer, 415V, outgoing MCCBs as per SLD. Incl. busbar, earth bar, DIN rail, metering provisions. Supply, install, test & commission. Connected load: 150.86 kW. | SLD | Nr | 1 | 32000 |  | 5F — 150.86 kW
A2.6 | SMDB-6F: Floor-standing SMDB, 300A TP MCCB 35kA incomer, 415V, outgoing MCCBs as per SLD. Incl. busbar, earth bar, DIN rail, metering provisions. Supply, install, test & commission. Connected load: 150.86 kW. | SLD | Nr | 1 | 32000 |  | 6F — 150.86 kW
A2.7 | SMDB-7F: Floor-standing SMDB, 300A TP MCCB 35kA incomer, 415V, outgoing MCCBs as per SLD. Incl. busbar, earth bar, DIN rail, metering provisions. Supply, install, test & commission. Connected load: 150.86 kW. | SLD | Nr | 1 | 32000 |  | 7F — 150.86 kW
A2.8 | SMDB-8F: Floor-standing SMDB, 300A TP MCCB 35kA incomer, 415V, outgoing MCCBs as per SLD. Incl. busbar, earth bar, DIN rail, metering provisions. Supply, install, test & commission. Connected load: 150.86 kW. | SLD | Nr | 1 | 32000 |  | 8F — 150.86 kW
Sub-Total A2
A3 — SMDBs — Ground Floor, Roof, Services & Emergency
A3.1 | SMDB-TF-odd (Emergency SMDB): Floor-standing emergency board, 300A TP MCCB 35kA incomer, fire-rated cable terminations, generator-backed via ATS. Supply, install, test & commission. | SLD | Nr | 4 | 60000 |  | 1F/3F/5F/7F — 150.86 kW
A3.2 | SMDB-TF-even (Emergency SMDB): Floor-standing emergency board, 300A TP MCCB 35kA incomer, fire-rated cable terminations, generator-backed via ATS. Supply, install, test & commission. | SLD | Nr | 4 | 60000 |  | 2F/4F/6F/8F — 150.86 kW
A3.3 | SMDB-RF (Emergency SMDB): Floor-standing emergency board, 500A TP MCCB 35kA incomer, fire-rated cable terminations, generator-backed via ATS. Supply, install, test & commission. | SLD | Nr | 1 | 80000 |  | Roof — 248.63 kW
A3.4 | SMDB-G (Emergency SMDB): Floor-standing emergency board, 125A TP MCCB 35kA incomer, fire-rated cable terminations, generator-backed via ATS. Supply, install, test & commission. | SLD | Nr | 1 | 25000 |  | Ground — 60.55 kW
A3.5 | SMDB-EV (Emergency SMDB): Floor-standing emergency board, 160A TP MCCB 35kA incomer, fire-rated cable terminations, generator-backed via ATS. Supply, install, test & commission. | SLD | Nr | 1 | 32000 |  | Basement — 88 kW
A3.6 | SMDB-SH01: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 15 kW
A3.7 | SMDB-SH02: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 15 kW
A3.8 | SMDB-SH03: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 15 kW
A3.9 | SMDB-SH04: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 15 kW
A3.10 | SMDB-SH05: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 25 kW
A3.11 | SMDB-SH06: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 10 kW
A3.12 | SMDB-SH07: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 10 kW
A3.13 | SMDB-SH08: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 40 kW
A3.14 | SMDB-SH09: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 10 kW
A3.15 | SMDB-SH10: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 15 kW
A3.16 | SMDB-SH11: Wall-mounted retail shop SMDB, 40A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 6000 |  | Ground — 15 kW
A3.17 | SMDB-SH12: Wall-mounted retail shop SMDB, 63A TP MCCB 35kA incomer, outgoing MCCBs for retail unit. Supply, install, test & commission. | SLD | Nr | 1 | 9000 |  | Ground — 30 kW
A3.18 | ESMDB-G (Emergency SMDB): Floor-standing emergency board, 400A TP MCCB 35kA incomer, fire-rated cable terminations, generator-backed via ATS. Supply, install, test & commission. | SLD | Nr | 1 | 80000 |  | Ground — 190.08 kW
A3.19 | ESMDB-RF (Emergency SMDB): Floor-standing emergency board, 160A TP MCCB 35kA incomer, fire-rated cable terminations, generator-backed via ATS. Supply, install, test & commission. | SLD | Nr | 1 | 32000 |  | Roof — 88.69 kW
Sub-Total A3
SECTION A — TOTAL

## B - Distribution Boards
BILL OF QUANTITIES — SECTION B: DISTRIBUTION BOARDS (DBs) & CONSUMER UNITS
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25
Item | Description | Reference | Unit | Qty | Unit Rate (AED) | Amount (AED) | Remarks
B1 — DISTRIBUTION BOARDS (per cable schedule)
B1.1 | DB-G: Distribution board fed from SMDB-G, 63A TP incomer. 4C 16mm2 XLPE/SWA/PVC +1C 16mm2 ECC | SLD | Nr | 1 | 32 |  | Ground
B1.2 | DB-F1: Distribution board fed from SMDB-G, 40A TP incomer. 4C 10mm2 XLPE/SWA/PVC +1C 10mm2 ECC | SLD | Nr | 1 | 22 |  | Ground
B1.3 | DB-F4: Distribution board fed from SMDB-G, 40A TP incomer. 4C 10mm2 XLPE/SWA/PVC +1C 10mm2 ECC | SLD | Nr | 1 | 22 |  | Ground
B1.4 | DB-F5: Distribution board fed from SMDB-G, 40A TP incomer. 4C 10mm2 XLPE/SWA/PVC +1C 10mm2 ECC | SLD | Nr | 1 | 22 |  | Ground
B1.5 | DB-L.GYM: Distribution board fed from SMDB-RF, 40A TP incomer. 4C 10mm2 XLPE/SWA/PVC +1C 10mm2 ECC | SLD | Nr | 1 | 22 |  | Roof
B1.6 | DB-G.GYM: Distribution board fed from SMDB-RF, 40A TP incomer. 4C 10mm2 XLPE/SWA/PVC +1C 10mm2 ECC | SLD | Nr | 1 | 22 |  | Roof
B1.7 | DB-WM: Distribution board fed from SMDB-RF, 40A TP incomer. 2C 10mm2 XLPE/SWA/PVC +1C 10mm2 ECC | SLD | Nr | 1 | 12 |  | Roof
B1.8 | EDB-G: Distribution board fed from ESMDB-G, 40A TP incomer. 4C 10mm2 FIRE RATED +1C 10mm2 ECC | SLD | Nr | 1 | 35 |  | Ground
B1.9 | EDB-1F: Distribution board fed from ESMDB-G, 32A TP incomer. 4C 6mm2 FIRE RATED +1C 6mm2 ECC | SLD | Nr | 1 | 22 |  | 1F
B1.10 | EDB-TEL: Distribution board fed from ESMDB-G, 40A TP incomer. 4C 10mm2 FIRE RATED +1C 10mm2 ECC | SLD | Nr | 1 | 35 |  | Ground
B1.11 | EDB-PR: Distribution board fed from ESMDB-G, 40A TP incomer. 4C 10mm2 FIRE RATED +1C 10mm2 ECC | SLD | Nr | 1 | 35 |  | Underground
B1.12 | EDB-4F: Distribution board fed from ESMDB-RF, 40A TP incomer. 4C 10mm2 FIRE RATED +1C 10mm2 ECC | SLD | Nr | 1 | 35 |  | 4F
B1.13 | EDB-7F: Distribution board fed from ESMDB-RF, 40A TP incomer. 4C 10mm2 FIRE RATED +1C 10mm2 ECC | SLD | Nr | 1 | 35 |  | 7F
B1.14 | EDB-GSM-R: Distribution board fed from ESMDB-RF, 40A TP incomer. 4C 10mm2 FIRE RATED +1C 10mm2 ECC | SLD | Nr | 1 | 35 |  | Roof
B1.15 | DB-T01 to DB-T15 (odd floors): Distribution board fed from SMDB-TF-odd, 40A TP incomer. 4C 16mm2 XLPE/SWA/PVC +1C 16mm2 ECC | SLD | Nr | 1 | 32 |  | 1F/3F/5F/7F
B1.16 | DB-T01 to DB-T15 (even floors): Distribution board fed from SMDB-TF-even, 40A TP incomer. 4C 16mm2 XLPE/SWA/PVC +1C 16mm2 ECC | SLD | Nr | 1 | 32 |  | 2F/4F/6F/8F
B1.17 | DB-SHOP01 to DB-SHOP12: Distribution board fed from SMDB-SH01 to SMDB-SH12, TP incomer. Internal distribution by tenant | SLD | Nr | 1 | 12000 |  | Ground
Sub-Total B1
SECTION B — TOTAL

## C - Main Cables (LV to SMDB)
BILL OF QUANTITIES — SECTION C: LV POWER CABLES — MAIN & RISING MAINS (LV Panel to SMDBs)
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25
Item | Description | Reference | Unit | Qty | Unit Rate (AED) | Amount (AED) | Remarks
C1 — XLPE/SWA/PVC LV CABLES (LV Panel to SMDB) — Supply & Install incl. fixings, glands, terminations
C1.1 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-1F (4C 150mm2 XLPE/SWA/PVC +1x1x70mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 25 | 195
C1.2 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-2F (4C 150mm2 XLPE/SWA/PVC +1x1x70mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 29 | 195
C1.3 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-3F (4C 150mm2 XLPE/SWA/PVC +1x1x70mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 33 | 195
C1.4 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-4F (4C 150mm2 XLPE/SWA/PVC +1x1x70mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 37 | 195
C1.5 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-5F (4C 150mm2 XLPE/SWA/PVC +1x1x70mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 41 | 195
C1.6 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-6F (4C 150mm2 XLPE/SWA/PVC +1x1x70mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 45 | 195
C1.7 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-7F (4C 150mm2 XLPE/SWA/PVC +1x1x70mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 49 | 195
C1.8 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-8F (4C 150mm2 XLPE/SWA/PVC +1x1x70mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 53 | 195
C1.9 | 4C × 185mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-TF-odd (1X4C 185mm2 XLPE/SWA/PVC +1C 95mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 45 | 245
C1.10 | 4C × 185mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-01 to SMDB-TF-even (1X4C 185mm2 XLPE/SWA/PVC +1C 95mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 45 | 245
C1.11 | 4C × 150mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-RF (2X4C 150mm2 XLPE/SWA/PVC +1X1C 150mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 65 | 195
C1.12 | 4C × 50mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-G (1X4C 50mm2 XLPE/SWA/PVC +1X1C 25mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 15 | 85
C1.13 | 4C × 70mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-EV (1X4C 70mm2 XLPE/SWA/PVC +1X1C 35mm2 ECC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 20 | 110
C1.14 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH01 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 20 | 22
C1.15 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH02 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 22 | 22
C1.16 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH03 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 24 | 22
C1.17 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH04 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 26 | 22
C1.18 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH05 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 28 | 22
C1.19 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH06 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 30 | 22
C1.20 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH07 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 32 | 22
C1.21 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH08 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 34 | 22
C1.22 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH09 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 36 | 22
C1.23 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH10 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 38 | 22
C1.24 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH11 (1X4C 10mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 40 | 22
C1.25 | 4C × 16mm² XLPE/SWA/PVC 600/1000V armoured cable — LVP-02 to SMDB-SH12 (1X4C 16mm2 XLPE/SWA/PVC). Installed in cable tray/ladder. Incl. cable glands, lugs, ferrules and terminations at both ends. | P-200 / P-201 | m | 42 | 32
Sub-Total C1 (XLPE/SWA)
C2 — FIRE-RATED (FR) CABLES — Emergency & Fire Services Rising Mains
C2.1 | 4C × 300mm² Fire-Rated (BS6387 CWZ / IEC 60331) cable — LVP-02 to ESMDB-G (4C 300mm2 FIRE RATED +1C 35mm2 ECC). Installed in dedicated fire-rated conduit/tray. | SLD | m | 15 | 616
C2.2 | 4C × 185mm² Fire-Rated (BS6387 CWZ / IEC 60331) cable — LVP-02 to Fire Pump (1X4C 185mm2 FP400 FIRE RATED +1C 95mm2 FR ECC, 350A TP). Installed in dedicated fire-rated conduit/tray. | SLD | m | 35 | 392
Sub-Total C2 (Fire Rated)
C3 — EARTH CONTINUITY CONDUCTORS (ECC) for Rising Mains
C3.1 | 1C × 35mm² bare/green-yellow XLPE ECC — alongside fire-rated cables. | SLD | m | 50 | 27 |  | Allow per FR run
C3.2 | 1C × 10mm²–70mm² bare/green-yellow XLPE ECC — alongside all XLPE rising mains. (Allow per run) | SLD | m | 785 | 6 |  | Estimate — confirm per run
Sub-Total C3 (ECC)
SECTION C — TOTAL

## D - Distribution Cables
BILL OF QUANTITIES — SECTION D: LV POWER CABLES — DISTRIBUTION (SMDB to DB)
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25
Item | Description | Reference | Unit | Qty | Unit Rate (AED) | Amount (AED) | Remarks
D1 — XLPE/SWA/PVC DISTRIBUTION CABLES — SMDB to DB
D1.1 | 4C × 16mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-G to DB-G. | SLD | m | 20 | 32
D1.2 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-G to DB-F1. | SLD | m | 15 | 22
D1.3 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-G to DB-F4. | SLD | m | 15 | 22
D1.4 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-G to DB-F5. | SLD | m | 15 | 22
D1.5 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-RF to DB-L.GYM. | SLD | m | 20 | 22
D1.6 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-RF to DB-G.GYM. | SLD | m | 20 | 22
D1.7 | 4C × 10mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-RF to DB-WM. | SLD | m | 15 | 22
D1.8 | 4C × 16mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-TF-odd to DB-T01 to DB-T15 odd floors. | SLD | m | 25 | 32
D1.9 | 4C × 16mm² XLPE/SWA/PVC 600/1000V armoured cable — SMDB-TF-even to DB-T01 to DB-T15 even floors. | SLD | m | 25 | 32
Sub-Total D1
D2 — EMERGENCY DISTRIBUTION CABLES (Fire Rated)
D2.1 | 4C × 70mm² Fire-Rated cable — ESMDB-G to ESMDB-RF. | SLD | m | 65 | 176
D2.2 | 4C × 10mm² Fire-Rated cable — ESMDB-G to EDB-G. | SLD | m | 15 | 35
D2.3 | 4C × 6mm² Fire-Rated cable — ESMDB-G to EDB-1F. | SLD | m | 25 | 22
D2.4 | 4C × 10mm² Fire-Rated cable — ESMDB-G to EDB-TEL. | SLD | m | 15 | 35
D2.5 | 4C × 10mm² Fire-Rated cable — ESMDB-G to EDB-PR. | SLD | m | 30 | 35
D2.6 | 4C × 10mm² Fire-Rated cable — ESMDB-RF to EDB-4F. | SLD | m | 20 | 35
D2.7 | 4C × 10mm² Fire-Rated cable — ESMDB-RF to EDB-7F. | SLD | m | 10 | 35
D2.8 | 4C × 10mm² Fire-Rated cable — ESMDB-RF to EDB-GSM-R. | SLD | m | 15 | 35
D2.9 | 4C × 10mm² Fire-Rated cable — ESMDB-RF to Lift-01. | SLD | m | 35 | 35
D2.10 | 4C × 10mm² Fire-Rated cable — ESMDB-RF to Lift-02. | SLD | m | 35 | 35
D2.11 | 4C × 10mm² Fire-Rated cable — ESMDB-RF to Lift-03. | SLD | m | 35 | 35
D2.12 | 4C × 10mm² Fire-Rated cable — ESMDB-RF to Booster Pump. | SLD | m | 20 | 35
Sub-Total D2
SECTION D — TOTAL

## E - Cable Management
BILL OF QUANTITIES — SECTION E: CABLE MANAGEMENT — TRAYS, LADDERS & CONDUITS
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25
Item | Description | Reference | Unit | Qty | Unit Rate (AED) | Amount (AED) | Remarks
E1 — CABLE TRAYS, LADDERS & CONDUITS
E1.1 | GI Hot-dip galvanised cable ladder, 500mm × 100mm side rail (vertical riser shaft, UG to Roof), c/w supports, brackets, bends, tees, fixings. | SLD | m | 40 | 640
E1.2 | GI Hot-dip galvanised cable ladder, 300mm × 100mm side rail (horizontal at each floor riser→SMDB), c/w supports, brackets, bends, tees, fixings. | SLD | m | 130 | 385
E1.3 | GI perforated cable tray, 200mm × 50mm (corridor distribution 1F–8F), c/w supports, brackets, bends, tees, fixings. | SLD | m | 400 | 310
E1.4 | GI perforated cable tray, 100mm × 50mm (branch distribution to DBs), c/w supports, brackets, bends, tees, fixings. | SLD | m | 300 | 160
E1.5 | GI perforated cable tray, 200mm × 50mm (Ground floor retail/common), c/w supports, brackets, bends, tees, fixings. | SLD | m | 100 | 310
E1.6 | GI perforated cable tray, 300mm × 75mm (Roof mechanical), c/w supports, brackets, bends, tees, fixings. | SLD | m | 80 | 385
E1.7 | 25mm uPVC conduit c/w draw wire, saddles, junction boxes, c/w supports, brackets, bends, tees, fixings. | SLD | m | 535 | 48
E1.8 | 32mm uPVC conduit (cable tray to SMDB at each floor), c/w supports, brackets, bends, tees, fixings. | SLD | m | 80 | 62
E1.9 | 20mm uPVC conduit (final-circuit drops to outlets), c/w supports, brackets, bends, tees, fixings. | SLD | m | 400 | 48
E1.10 | 25mm GI rigid conduit — fire-rated for emergency cable routes (staircase wells, fire shafts), c/w supports, brackets, bends, tees, fixings. | SLD | m | 200 | 77
Sub-Total E1
SECTION E — TOTAL

## Summary of BOQ
BILL OF QUANTITIES — SUMMARY
Proposed B+G+8+R Commercial & Residential Building ¦ Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ FA_P379 / CRs B/010/25
Section | Description | Sheet Ref | Sub-Total (AED) | Notes
A | LV Switchgear & Sub-Main Distribution Boards (SMDBs) | Sheet A | 0 | LV panels, ATS, gen, SMDBs
B | Distribution Boards (DBs) & Consumer Units | Sheet B | 0 | Apt + comm + retail + emerg
C | LV Power Cables — Main & Rising Mains (LV→SMDB) | Sheet C | 0 | XLPE/SWA + Fire-Rated + ECC
D | LV Power Cables — Distribution (SMDB→DB) | Sheet D | 0 | Distribution cables + bulk
E | Cable Management — Trays, Ladders & Conduits | Sheet E | 0 | GI ladder, tray, conduit
F | Earthing & Bonding | Sheet F | 0 | Earth pits, MEB, conductors
G | Sundries, Accessories & T&C | Sheet G | 0 | Labels, fire stop, T&C, DEWA
SUB-TOTAL (Sections A–G) |  |  | 0
Contingency (10%) |  |  | 0
VAT (5%) |  |  | 0
GRAND TOTAL (incl. Contingency & VAT) |  |  | 0
INSTRUCTIONS: Enter unit rates (AED) in column F of each section sheet. Per-row Amounts and section totals roll up here automatically.

## F - Earthing & Bonding
BILL OF QUANTITIES — SECTION F: EARTHING & BONDING
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25
Item | Description | Reference | Unit | Qty | Unit Rate (AED) | Amount (AED) | Remarks
F1 — MAIN EARTHING SYSTEM
F1.1 | Main earth bar (MEB) in LV room — 50×6mm copper busbar, drilled and labelled, c/w insulators and fixing | SLD | Nr | 2 | 14
F1.2 | Earth pit (BS 7430 / DEWA) — 1200mm copper-bonded steel earth rod, inspection chamber, backfill, conductor clamp. Test < 1 Ω | SLD | Nr | 4 | 640
F1.3 | 1C × 95mm² bare copper earth conductor — MEB to earth pits and DEWA earth terminal | SLD | m | 30 | 36
F1.4 | 1C × 50mm² green/yellow PVC earth conductor — MEB to structural steel bonding points, water/gas entry | SLD | m | 40 | 23
F1.5 | 1C × 35mm² green/yellow XLPE earth conductor — MEB to sub-earth bar at each SMDB | SLD | m | 400 | 17
F1.6 | 1C × 10mm² green/yellow PVC earth conductor — SMDB earth bar to each DB on residential floors | SLD | m | 600 | 6
F1.7 | Supplementary bonding conductor 4mm² — pipework, trays, equipment frames (provisional) | SLD | Item | 1 | 11
Sub-Total F1
SECTION F — TOTAL

## G - Sundries & T&C
BILL OF QUANTITIES — SECTION G: SUNDRIES, ACCESSORIES & TESTING/COMMISSIONING
Project: Proposed B+G+8+R Commercial & Residential Building, Plot 6731315, Al Barsha South Third, Dubai, UAE ¦ Job: FA_P379 / CRs B/010/25
Item | Description | Reference | Unit | Qty | Unit Rate (AED) | Amount (AED) | Remarks
G1 — ACCESSORIES & SUNDRIES
G1.1 | Cable identification labels — self-adhesive ferrules at both ends. Include as-installed labelling matching cable schedule. | — | Item | 1 | 18000
G1.2 | Cable cleats and ties — stainless steel, max 400mm spacing on vertical runs and 900mm on horizontal. | — | Item | 1 | 510
G1.3 | Fire stopping — intumescent compounds, collars, pillows at all cable penetrations through fire-rated walls/slabs/risers. Restore fire rating. | — | Item | 1 | 28000
G1.4 | Smoke / fire barriers at all electrical-riser floor penetrations — proprietary fire-rated barrier system. Allow per floor. | — | Nr | 12 | 4500
G1.5 | Temporary power supply during construction — provisional sum. | — | Sum | 1 | 85000
Sub-Total G1
G2 — TESTING & COMMISSIONING
G2.1 | Insulation resistance testing (500V Megger) of all LV cables. Report included. | DEWA/IEC | Item | 1 | 18000
G2.2 | Continuity and polarity testing of all circuits. | DEWA/IEC | Item | 1 | 12000
G2.3 | Earth fault loop impedance testing at all boards. | DEWA/IEC | Item | 1 | 8500
G2.4 | RCD testing at all RCD-protected circuits. | DEWA/IEC | Item | 1 | 5500
G2.5 | ATS changeover testing — simulate mains failure, verify auto-switchover. Include full load test. | DEWA/IEC | Item | 1 | 80000
G2.6 | Power factor correction verification — record PF before/after capacitor bank energisation. | DEWA/IEC | Item | 1 | 8500
G2.7 | Full DEWA inspection and approval — application fees, inspections, rectifications until final approval. Provisional sum. | DEWA/IEC | Sum | 1
G2.8 | As-built drawings (AutoCAD + PDF) and O&M Manuals — full set for LV distribution system. | DEWA/IEC | Item | 1 | 38000
Sub-Total G2
SECTION G — TOTAL